## README
NA model scenario quantification plan - v2
Prepared 2026-09-18 for the 14 requested SE North America scenarios / sensitivities. Status: PLAN (nothing implemented). Numbers come from web-sourced reports (2025-2026 vintage) plus the model baseline; every number in "Assumptions" carries a source id or is explicitly marked as an assumption.
Sheets
Overview - one row per scenario: direction, model levers, implementation route, REPRESENTABILITY flag (can the model do it), EVIDENCE strength (how well sourced - informational, not a value judgement), overlap with existing sensitivities, proposed variants incl. a stretch what-if, effort.
Assumptions - the quantified inputs per scenario (parameter, region, years, value, unit, derivation, source id, confidence, invented flag). This is what gets implemented.
Feasibility - concerns per scenario with a Type column: model = representation limitation (drives the flag), data = evidence note (does not drive the flag). Flags: GREEN = existing levers; YELLOW = needs a new lever/technology or an approximation; RED = cannot be represented. v2 (2026-09-18): judgement calls and far-fetched what-ifs are legitimate scenario content and are not down-rated; every scenario has a stretch variant; fusion capex = user input.
Sources - reference list (id, organisation, title, date, URL, used for).
Model baseline - what the model currently assumes (FEL26 base demand, funnels, costs, policy), so the deltas are visible.
Existing sensitivities - the v6 sensitivity set the new scenarios can reuse.
Open questions - decisions needed from the requesters before implementation.
Conventions
Regions: California, WECC (rest of US West), ERCOT, SPP, MISO, SERC (US Southeast), PJM, NewYork, NewEngland, Canada (one node). Years 2025-2040 annual. Demand in TWh busbar. Costs in EUR2023 (1 USD = 0.925 EUR). Gas prices in USD/MMBtu where quoted; 1 USD/MMBtu = 0.877 EUR/GJ.
Effort: S = data rows via existing scripts (<1 day incl. run); M = new script/lever or new technology (1-3 days); L = new model feature or FEL demand-model rerun by the FEL team (>3 days / external dependency).
Tags from the request: [Tailwind] upside to load / SE market, [Headwind] downside, [Mixed].

## Overview
ID | Scenario | Tag | What it means for the model | Model levers (parameters) | Implementation route | Representability | Representability summary | Evidence strength (info) | Overlap with existing sensitivities | Proposed variants (incl. stretch) | Effort | Key external anchors
1 | EVs come back with a vengeance | Tailwind | Transport electricity above the FEL26 base after 2027. Base Power_BEVs (US) = 25/71/213/442 TWh in 2025/30/35/40. Anchors: EIA AEO2026 reference (embeds EPA MY2027+ standards, BEV ~50 % of sales by 2032) = 146/408/624 TWh; EEI 2024 pre-OBBBA path (72 % share, 78.5 M EVs by 2035) as the stretch. | Par_SpecifiedAnnualDemand Power_BEVs per region/year (BEV charging profile exists). Canada Power_BEVs to the CER EF2026 net-zero path. | Preferred: FEL demand model preset bev_share = high (FEL team). Fallback: scale Power_BEVs rows after convert_fel_to_demand (our side, 1 script). | GREEN | Existing demand lever with a real charging profile. Regional split of the increment follows the FEL geography (optional ACC II tilt). | High - EIA/EEI/CER paths, quarterly sales data, state registration shares | None of the v6 sensitivities changes BEVs. | 1A AEO2026 policy path (US 146/408/624 TWh; Canada 29/72/125). 1B = 1A + commercial-vehicle acceleration (x1.25 on LCV/MHDV/bus share). 1C stretch = EEI 2024 path (~+35 % over 1A by 2035, 2040 extrapolated: ~850 TWh) = "every second new car electric by 2030". | S | EIA AEO2026 Tables 2/38/39; EEI 2024; Cox Q1-Q2 2026; Argonne; Alliance FY2025; CER EF2026; BNEF EVO 2026 (17 % = downside context)
2 | Hydrogen comes back with a vengeance | Tailwind | Electrolysis load re-accelerates. Base Power_Hydrogen (US) = 2/6/6/6 TWh (~0.1 Mt electrolytic, flat). Anchors: DOE 3.8 GW firm electrolyser pipeline (~27 TWh), DOE 10/20 Mt clean-H2 strategy, 55.5 kWh/kg; the electrolytic share of clean H2 is the scenario dial. | Par_SpecifiedAnnualDemand Power_Hydrogen per region/year (profile FLAT). Optional: flexible electrolyser technology (X_Electrolyser + H2 storage) so the load follows cheap hours. | FEL preset hydrogen_scenario = high, or our rows (hub-based regional split). | YELLOW | Demand lever exists. The only model-side limitation: electrolysis is a flat, inflexible load; at 300-550 TWh the model over-builds firm capacity for it. A flexible-electrolyser technology fixes that (M-L effort). | Medium - pipeline and targets sourced; electrolytic share and hub split are judgement | None. | 2A "45V reignites": US 10/27/165/333 TWh (2028/30/35/40) = 3.8 GW firm by 2030, 3 Mt electrolytic 2035, 6 Mt 2040 (30 % of DOE 20 Mt); Canada CER Current Measures 25/52/80. 2B = half of 2A. 2C stretch = 10 Mt electrolytic by 2040 (50 % of the DOE target) = 555 TWh, Canada CER net-zero 3.0 Mt = 165 TWh. 2D = 2A with flexible electrolysers (later). | S (2A-2C), M-L (2D) | DOE Record 24001; DOE H2Hubs status Apr 2026 (5 hubs, $4.8 bn); DOE strategy 10/20/50 Mt; IEA GHR 2025; AEO2026 HMM; CER EF2026
3 | The Age of Compute - AI is only phase one | Tailwind | Compute demand keeps compounding beyond the current DC wave (agentic AI, Web3/crypto, robotics/dark factories, 5G/6G, defense AI). Calibration: FEL26 base DC (US 726/1,344/1,817 TWh) sits at the upper-middle of external forecasts (LBNL 2026 reference 649 TWh 2030; BNEF 194 GW 2035 ~ 1,450 TWh); dc_high (2,188/3,585) is above all of them - which is exactly the space a "phase two" scenario is meant to explore. | Power_DataCenter path (base -> BNEF 2035 -> +9 %/yr, or dc_high) plus second-wave flat loads (crypto, robotics/dark factories, telecom/edge, defense AI) as Power_General adders or a new Power_Compute_Other fuel with its own reporting. | DC path: FEL preset dc_scenario or our rows. Second-wave adders: our rows (flat profile). | GREEN | Pure demand lever. Horizon ends 2040, so "well beyond the current wave" is visible only through the steepness of the 2030-40 path and the adders. | Medium - DC forecasts abundant; second-wave loads: crypto sourced, robotics = global number with assumed US share, telecom/edge/defense = stylised | dc_high, dc_high_limitless, btm_lag. | 3A "sustained": DC 726/1,450/2,230 TWh + adders crypto 60->80, robotics 5->90->150, telecom/edge/defense 10->50 TWh (US 2040 ~ +280 TWh). 3B = dc_high + same adders. 3C stretch "compute super-cycle": dc_high + adders x3 (crypto 200, robotics 450, telecom/defense 150 TWh by 2040) and DC funnel caps lifted (dc_high_limitless logic). | S | LBNL 2025 Update (Jun 2026); BNEF Jul 2026; McKinsey NASEO 2026; EPRI 2026; CCAF Jun 2026; Wood Mackenzie Aug 2026 (robotics 363 TWh global 2035); Grid Strategies Nov 2025
4 | A space race is coming | Tailwind | Commercial space as an industrial and energy-demand driver: launch cadence (FAA: 25 Starship/yr Starbase, 76/yr SLC-37; S-1 ambition "thousands of launches/yr"), propellant production (~5,000 t/launch; S-1 names air-separation/liquefaction plants and power supply as scale-up constraints; Starbase 250 MW gas plant in the EA), Starbase/Starfactory manufacturing, orbital compute (SpaceX satellites from 2028, "100 GW/yr" ambition; Starcloud 5 GW), xAI Colossus ~1 GW (Memphis). The existing space_dc trio models orbital compute as a REDUCTION of terrestrial DC load; the tailwind reading adds the terrestrial industrial chain. | Power_General adders (flat) in ERCOT (Starbase), SERC (Cape/Florida, Memphis), California (Vandenberg, manufacturing), WECC; e-propellant production as an electricity load (electrolytic H2 + DAC CO2 -> CH4) - representable as a flat load or as Power_Hydrogen-type demand; orbital compute via the existing space_dc trio (sign: minus). | Our rows; existing space_dc workbooks for the orbital leg. | GREEN | Everything here is a flat demand adder the model handles trivially. Materiality is a scenario choice: fossil-propellant launches are small (~2 GWh/launch), an e-propellant / mass-manufacturing space economy is large (tens to hundreds of TWh) - both can be run. | Low-Medium - cadence, Starbase power plant and S-1 statements sourced; site loads and manufacturing MW not published; e-propellant chain is a derivation | space_dc, space_dc_disruptive, space_dc_spacex (orbital compute removes 5/13/27 % of US DC load by 2040). | 4A = existing space_dc trio (orbital compute displaces). 4B "terrestrial space industry, fossil propellant": +0.5 GW ERCOT, +0.3 GW SERC, +0.2 GW California flat by 2035 (~8 TWh). 4C stretch "e-propellant space economy": 1,000 launches/yr by 2035, 5,000 by 2040 with synthetic methane (electrolytic H2 + DAC CO2, ~20 GWh/launch) = 20 -> 100 TWh, plus satellite/launcher manufacturing 10 -> 40 TWh and orbital-compute ground segment 5 -> 15 TWh, located ERCOT 50 %, California 20 %, SERC 20 %, WECC 10 %; combined with 4A-spacex (orbital compute -27 % of DC). | S | SpaceX S-1/A (May-Jun 2026); FAA Starbase EA (250 MW plant) and SLC-37 ROD (Nov 2025); Starcloud FCC filing; Google Suncatcher; NREL/DOE electrolysis 55 kWh/kg; DAC ~2 MWh/t CO2 (Climeworks/NASEM range)
5 | Political brakes on build-out | Headwind | Local opposition + midterms stall DC development and new fossil generation. Sourced: Gallup Mar 2026 71 % oppose local AI DCs; Data Center Watch $156 bn blocked/delayed in 2025, $130 bn in Q1 2026; 632 jurisdictions with formal action (270 adopted moratoria), statewide bills in 14 states; NY EO 62; Texas paused ~49.8 GW of ERCOT DC interconnections (Aug 2026), BNEF expects ~8.25 GW ERCOT DC adds through 2030; gas: turbine lead times 5-7 yr, GE Vernova slots into 2031, Chestnut Run 1.2 GW without turbines, Dominion Chesterfield to 2029. | Regional Power_DataCenter multipliers on the base increment; GroupTotalAnnualMaxNewCapacity for gas techs (US-wide cap); gas guardrail minimum removed; RES funnel max = announced pipeline. | Our rows (demand) + add_capacity_bounds options (funnel) + one group-cap row set. | GREEN | All levers exist (demand, funnels, group caps). | Medium-High - opposition metrics, ERCOT pause and turbine constraints sourced; regional multipliers and the gas haircut are dials | dc_low (national cut, no supply constraint); scenario 5 is regional plus supply-side. | 5A brakes 2027-2040 (regional DC multipliers, gas cap 10 GW/yr US 2027-31, RES max = pipeline). 5B brakes released after 2030. 5C stretch "national moratorium": DC frozen at the 2027 level through 2032 then +3 %/yr, gas cap 5 GW/yr 2027-2035, no new coal/gas permits in NY/NE/CA (max = residual). | M | Gallup 709772; Data Center Watch 2025 YIR + Q1 2026; GatherGov Sep 2026; NY EO 62; Utility Dive/BNEF Aug 2026; GE Vernova Q2 2026; IIR Sep 2025; OBBBA credit dates
6 | A multi-year Strait of Hormuz problem | Mixed | 2-3+ year Gulf disruption. Facts (Sep 2026): strait effectively closed since 2 Mar 2026 with partial re-openings; Brent ~$100; Ras Laffan 12.8 Mtpa offline 3-5 yr; TTF $16-24/MMBtu; Henry Hub so far ~+10 % (IMF) because US LNG exports are liquefaction-bound (17.4 Bcf/d, capacity 21.2 Bcf/d 2028, 28.7 Bcf/d 2029); Fed hiked Sep 2026; Fitch: NA utilities "deteriorating"; ~60 % of solar / 50 % of battery projects delayed early 2026. WoodMac extended disruption: Brent ~$200; Dallas Fed 3-quarter closure: +1.1 pp PCE. | (a) LNG channel: Gas_Export demand at liquefaction capacity (NorthAmerica_gas scenario) or a Henry Hub price path in the folded fuel cost; (b) macro channel: TechnologyDiscountRate uplift, capex uplift decaying, IC growth cap (grid_low logic), demand = recession FEL; (c) oil-to-EV link (scenario 1 coupling). | (a) NorthAmerica_gas overlay rows; (b) our rows via existing scripts. | YELLOW | The model has no macro or utility-behaviour module: inflation, rates and rate freezes must be translated into exogenous cost, discount-rate, build-cap and demand dials. That translation is the scenario definition, and both mild and severe settings can be run. | Medium - price scenarios and macro effects sourced; the utility capex-freeze behaviour has no direct model counterpart | recession (demand), grid_low (IC cap), NorthAmerica_gas (explicit exports). | 6A LNG pull (exports at 95 % of capacity + 5 Bcf/d extra FID wave by 2032; HH +10 % 2026-27, +$2/MMBtu 2027-29). 6B macro freeze (WACC +150 bp 2026-30, capex +15 % 2026-28 -> 0 by 2032, IC 0.75 %/yr 2026-30, recession demand 2026-30). 6C = 6A + 6B. 6D stretch "1970s replay": HH +$4/MMBtu 2027-2031, WACC +300 bp 2026-32, capex +30 % 2026-29, IC growth 0 2026-30, recession demand through 2032, plus EV 1A coupling (oil at $150+). | M | WoodMac 20 May 2026; Dallas Fed Mar/Apr/Jun 2026; EIA STEO Sep 2026; IMF WEO Jul 2026; OECD Jun 2026; IEA GMR Q3 2026; EIA liquefaction capacity; Fitch Jun 2026; GridLab/WoodMac turbine prices; EIA MER 7.6
7 | A generation/storage technology breakthrough | Headwind to GS | SMRs, fusion, LDES or non-lithium chemistries arrive faster/cheaper and displace gas turbines. Base: SMR = 0 before 2033, 2.9 GW 2035, 18.7 GW 2040, capex 9,091 EUR/kW flat; redox flow from 2030; no iron-air, no fusion. FUSION CAPEX: to be supplied by the user (placeholder rows in Assumptions). | P_Nuclear_SMR: TotalAnnualMaxCapacity brought forward and raised, capex learning path. New storage S_/D_IronAir (100 h). Li-ion/Na-ion: reuse bess_optimistic. New technology P_Fusion (capex/FOM/availability from the user; CF, lifetime, zero fuel cost, zero CO2, regional caps proposed here). | SMR: add_capacity_bounds option + cost rows. Iron-air and fusion: new technologies (sets, filter files, cost rows, E2P) - M each. | YELLOW | SMR and Li-ion legs use existing levers (GREEN). Iron-air and fusion need new technology entries (data-driven, region-agnostic - the model supports it, M effort each). Storage capex units must be converted to the model convention before writing iron-air rows. | Medium-High for SMR/LDES (INL/ATB cost bands, project pipeline, Form/Eos numbers); fusion capex = user input | bess_optimistic, nuclear_announced. | 7A SMR fast (available 2030; max 2/5/15/40 GW 2030/32/35/40; capex 5,090/3,980/3,330 EUR/kW). 7B = 7A + iron-air LDES (from 2028; $60->$30->$20/kWh; 0.5->5 GW/yr). 7C = 7B + bess_optimistic + fusion (user capex; proposed availability 2033, max 2/10 GW 2035/40). 7D stretch "everything early": SMR max 10/40/100 GW (2032/35/40) at the INL advanced path, iron-air unlimited build from 2030 at $20/kWh, fusion max 5/40 GW (2035/40) and 50 % lower capex than the user central value, Na-ion Li-ion x0.3 by 2035. | M | INL / NREL ATB 2025; DOE Liftoff Advanced Nuclear 2024; OPG Darlington; TVA Clinch River; TerraPower Natrium; Form Energy 2026; NREL ATB 2025 storage; Lazard LCOE+ 2026; CFS ARC; Helion; Tang et al. Nature Energy 2026 (for context only)
8 | Canada is the next data-center frontier | Tailwind | Alberta hyperscale build-out: Meta Sturgeon 1 -> 1.8 GW (> C$13 bn, Jul 2026) with the 932 MW Greenlight CCGT (FID Jul 2026, COD 2H 2030); AESO interim 1.2 GW to 2028, Phase 2: 20.7 GW proposed, 4.8 GW viable, 1.6 GW interruptible pool; Wonder Valley 7.5 GW / C$70 bn; Canada > 20 GW pipeline (18 GW Alberta); ISED: 5.5 GW needed by 2030. Base check: FEL26 Canada DC = 17/71/178/269 TWh (2/8/20/31 GW average), which already exceeds a pipeline-consistent path (~41/130/220 TWh). A true tailwind must therefore go beyond the FEL base: Alberta as a continental hub. | Canada Power_DataCenter path; P_Gas_CCGT Canada TotalAnnualMinCapacity (bring-your-own-power plants); optional Canada gas funnel max lifted. | Our rows; funnel via add_capacity_bounds (Canada block). | GREEN | Demand and forced-gas levers exist. Canada is one node (Alberta gas vs Quebec hydro averaged; interruptible/gas-only rules not representable) - acceptable for a national view. | Medium-High to 2030 (announced projects, AESO rules), extrapolated after; the FEL base itself is the weakest number | dc_high/dc_low scale Canada with the US ratios. | 8A pipeline-consistent (Canada DC 41/130/220 TWh + BYOP gas minima +0.25/+0.93/+1.4 GW 2028/30/33) - below the FEL base, useful as the "what the announcements support" case. 8B = FEL base (269 TWh 2040). 8C stretch "Alberta continental hub": all 20.7 GW Alberta proposals + Wonder Valley 7.5 GW + ON/QC/BC 4 GW = 32 GW by 2035 (240 TWh), 45 GW by 2040 (335 TWh), with 10 GW of BYOP gas minima by 2035 and Canada-US IC growth x2 (grid_high logic). | S | Meta/Alberta Jul 2026; Greenlight FID Jul 2026; AESO Jun 2025 + Phase 2 (The Logic Jun 2026); Wonder Valley; ISED Jan 2026; IESO 2025 APO; Hydro-Quebec Feb 2026; BC Hydro
9 | Water scarcity triggers an artificial-water-production boom | Tailwind | Desalination, reuse, conveyance and cloud seeding add electricity demand. Sourced pipeline: Corpus Christi 30 MGD, Harbor Island 100 MGD, Doheny 5 MGD, Pure Water SoCal 115->150 MGD, Pure Water LA 230 MGD, Phoenix AWP 8 -> ~100 MGD, Arizona Gulf-of-California desal (earliest 2031; IDE proposal 300 kAF/yr = 1.0 Mm3/d), Texas Water Fund $20 bn 2027-47, Colorado River mandatory cuts 1.25 MAF/yr 2027-28 (ROD 21 Aug 2026), interstate exchange MOU Jun 2026. Energy: SWRO ~3.2 kWh/m3, brackish 0.4-1.2, RO reuse 0.84, conveyance up to 3.6. | Power_General adders (flat) in ERCOT, California, WECC (and SERC/Florida for a stretch case). | Our rows. | GREEN | Trivial to represent. Sourced pipeline is small (~4 TWh); the scenario dial is how far the Southwest goes toward Israeli/Gulf-style manufactured water. | High for the project pipeline and energy intensities; boom multipliers are dials | None. | 9A sourced pipeline (~3.7 TWh 2040). 9B boom = 10x (~37 TWh 2040). 9C stretch "manufactured water Southwest": 10 Mm3/d desal + conveyance across CA/AZ/NV/TX by 2040 (Israel today ~2 Mm3/d; Gulf states ~20) x 6.5 kWh/m3 = ~24 TWh, plus 2 Mm3/d Florida SWRO (5 TWh), plus 50 % of Colorado River deficit replaced by pumped imports (~1.5 MAF/yr x 3.6 kWh/m3 = 6.7 TWh) = ~36 TWh, concentrated in WECC/California/ERCOT/SERC. | S | USBR/DOI Aug 2026; TWDB; Texas Tribune Jun 2026; Inside Climate News Jun 2026; MWD Sep 2025; LADWP; KJZZ Nov 2025; Giammar et al. 2022; SRP MOU Jun 2026; IDRA handbook 2025-26
10 | Climate-driven relocation and rebuild | Mixed | Extreme weather relocates population from the South/coasts and drives rebuild and hardening. Sourced: Climate Central 2025 = 23 billion-dollar disasters, $115 bn (2024: 27; 2023: 28; H1 2025: 14); First Street: 55 M Americans expected to relocate by 2055 (5.2 M in 2025), insurance +29.4 %, $1.47 tn value loss, gainers ND/MT; Census V2025 still shows net inflows to NC/SC/TX/FL today (the scenario posits the reversal); Duke Florida $16 bn 5-yr plan, Entergy $15 bn/10 yr hardening; Deloitte 2026: peak +26 % by 2035; CDD +10-80 % across NA (Nature Comm 2026). | Regional re-allocation of Power_General (SERC/ERCOT/California -> MISO/PJM/NewEngland/NewYork/WECC-north); cooling uplift on Sunbelt General (Power_Buildings_Cooling profile exists but the category is empty in FEL data); TradeCapacityGrowthCosts uplift in coastal regions; accelerated retirement / lower availability of coastal plants (ResidualCapacity, AvailabilityFactor); rebuild construction load adder; planning-reserve parameter (set_peaking_res_cf). | Our rows (small re-allocation script) + cost/availability rows. | YELLOW | Representable with existing demand, cost and availability levers. Two model-side limitations: cooling cannot be separated from General (FEL data), and distribution-side hardening spend is invisible (only inter-regional transmission cost exists). The relocation shares are the scenario dial and can be as bold as wanted. | Low-Medium - migration and disaster statistics sourced; the regional relocation split and the rebuild load are stylised | None. | 10A mild: 2 % (2035) / 4 % (2040) of SERC+ERCOT+California General load re-allocated north; Sunbelt cooling +3 %; coastal IC cost +25 %. 10B hardening only (no relocation). 10C stretch "Great Reshuffle": 10 % (2035) / 20 % (2040) of Sunbelt General + DC growth re-allocated to MISO/PJM/NewEngland/NewYork/WECC-north; Sunbelt cooling +8 %; coastal IC cost +50 %; coastal gas/nuclear availability -5 pp from 2030 (storm outages); rebuild load +1 % of national General 2030-40; peaking reserve requirement +5 pp in SERC/ERCOT. | M | Climate Central Jan 2026; First Street Feb 2025; Census V2025 Jan 2026; Duke Energy Florida 2025; Entergy; Deloitte 2026; Nature Comm 2026
11 | FEOC restrictions on the Bulk-Power System | Tailwind (domestic OEMs) | EO 14421 (26 Aug 2026; circulated as 14420) restricts China-linked BPS equipment >= 69 kV incl. transformers, inverters, BESS; DOE rules due ~Dec 2026. OBBBA FEOC thresholds: storage 55 % (2026) -> 75 % (2030) non-PFE content. Costs: BNEF Dec 2025 stationary packs $70/kWh global, North America +44 %; tariff stack on Chinese ESS ~25 % (301) + 15 % (122); inverters ~+2 % of project capex; transformers +77 % price since 2019, lead times 128-144 weeks; domestic cells 20 -> 140 GWh/yr by 2028; WoodMac/ACP: 2026 storage installs below 2025 (18.9 GW). | Capex multipliers on D_/S_Battery_Li-Ion, PV (inverters), wind (generators/transformers), TradeCapacityGrowthCosts (transformers); Par_AnnualMaxNewCapacity for Li-ion 2026-27; optional forced replacement programme as a capex adder. | add_bess_cost_paths pattern + our rows. | GREEN | Cost and build-limit levers exist. The model reports capacity built and its capex (by technology and region), which is the proxy for domestic OEM demand; equipment origin and replacement of installed foreign gear are outside the model unless added as an exogenous capex adder (11C). | High - order text, thresholds, price premiums and domestic capacity all sourced; decay path is a dial | bess_pessimistic, grid_low. | 11A cost premium (Li-ion x1.44 2026 -> x1.30 2028 -> x1.15 2030 -> x1.05 2035; PV x1.02 2026-30; IC cost x1.30 2026-30 -> x1.10 2035; Li-ion adds capped 17 GW/yr 2026-27). 11B premiums persist (x1.15 through 2040). 11C stretch "rip-and-replace": 11B + Li-ion cap 12 GW/yr 2026-28 + wind/solar capex x1.10 2026-30 + an exogenous replacement programme (80 % of installed Chinese-origin inverters/BESS/transformers replaced 2028-2035, reported as capex outside the optimisation). | S (11A/B), M (11C) | EO 14421; Baker Tilly FEOC table; BNEF Dec 2025; Gateway Lines; WoodMac/PV Tech Aug 2026; WoodMac transformers; ACP May 2026; WoodMac/ACP ESM 2026; IIR Aug 2026
12 | AI overbuild correction | Headwind | Utility DC forecasts prove overstated. Sourced: Grid Strategies Nov 2025 - utility DC forecasts overstated by ~25 GW (~40 %); LBNL 2026 low case 521 TWh in 2030; WoodMac Aug 2026: 298 of 1,066 GW requested (28 %) committed; Bernstein 135 of 492 GW credible; Data Center Watch $130 bn blocked/delayed Q1 2026; Exelon/AEP/PJM forecast cuts 40-50 %. | Power_DataCenter path (national multiplier or plateau); optional stranded-asset view (gas built for DCs runs at low CF). | FEL preset dc_scenario = low, or our rows. | GREEN | Pure demand lever. | High | dc_low, recession. | 12A mild: DC US 540/620/690 TWh (2030/35/40) = LBNL low 2030 then +2 %/yr. 12B = existing dc_low (369/805/874). 12C stretch "AI winter": DC peaks 2028 at ~400 TWh, falls to 300 TWh by 2032 (capex bust, consolidation), recovers to 500 TWh by 2040; Canada same ratio. | S | Grid Strategies Nov 2025; LBNL 2025 Update; WoodMac Aug 2026; Bernstein; Data Center Watch Q1 2026; Bloomberg/Sightline Apr 2026
13 | Reindustrialization / onshoring as an independent load engine | Tailwind | Fabs, metals, defense and critical minerals add high-load-factor demand independent of DCs. Sourced: TSMC Arizona 6 fabs ($165 bn), Micron Clay NY 4 fabs ($100 bn, groundbreaking Jan 2026), Micron Boise, Samsung Taylor, TI Sherman, Intel Ohio (2030+); Century/EGA Inola OK smelter 750 kt/yr (~10.7 TWh/yr); ERCOT queue 474 GW with ~10 % non-DC (~45 GW); TSMC 37.1 kWh per 12-inch wafer mask layer (~3 MWh/wafer, ~3.6 TWh/yr per 100k-wafer/month fab); AEO2026 reference industrial electricity 1,059 -> 1,162 TWh. | Power_General adders (flat) per region, or a new fuel Power_Industry_Large with a flat profile for separate reporting; optional FEL industry-electrification uplift (Chemicals/Iron&Steel/Other) as a multiplier. | Our rows (project list -> region/year TWh); FEL preset industry_electrification_* for the electrification leg. | GREEN | Flat loads are the easiest thing the model does. Coordination item: FEL base industry growth may already contain some announced projects (question to the FEL team), which changes the adder size, not the representability. | Medium - project list sourced, per-fab MW derived, queue realisation and "other reshoring" are dials | None. | 13A announced projects + 25 % of the ERCOT non-DC queue: +62/+146/+165 TWh (2030/35/40). 13B 50 % queue realisation, doubled other-reshoring adders (~+230 TWh 2040). 13C stretch "industrial superpower": 13B + FEL industry electrification preset high (+20 % on industrial General by 2040 = ~+250 TWh) + defense/shipbuilding/munitions +20 TWh + critical-minerals refining +30 TWh (lithium, copper, rare earths in SPP/WECC/SERC) = ~+530 TWh by 2040. | S | TSMC 2024 AR; Micron/NIST/NYS PSC; Century/EGA Jan 2026 + DOE; IAI; ERCOT Apr 2026 + RTO Insider Sep 2026; EIA AEO2026 Table 2
14 | Decarbonization re-accelerates | Tailwind | Post-2028 policy swing + corporate 24/7 CFE + 45Q pull clean-firm, CCUS-on-gas and nuclear forward. Sourced: 45Q $85/t point-source (12 yr, indexed from 2027, transferable); NETL: NGCC + 90 % capture TOC $2,049/kW vs $952 (2018$), $55-61/t; Sutter 550 MW, Baytown 810 MW, Cane Run lost OCED awards May 2025; hyperscaler nuclear 9.8 GW in 13 deals (Meta 6.6 GW by 2035, Crane 835 MW 2027, Duane Arnold 615 MW 2029, Google-Kairos 500 MW, Amazon-X-energy 5 GW); Fervo 500 MW; EO 14302 (400 GW by 2050, +5 GW uprates by 2029); state 100 % targets (NY 2040, CT 2040, NJ 2035, CA 2045, WA 2045); IEA WEI 2026 clean $2.2 tn. Base: no CO2 price, no CES, P_Gas_CCS disabled, 45Y/48E ended for wind/solar. | Par_EmissionsPenalty (CO2 price path); capex multipliers (restored ITC); P_Gas_CCS enabled (max path, capex existing, 45Q as negative VariableCost); CCS retrofit technology (new); nuclear minima; Par_RegionalAnnualEmissionLimit / AnnualEmissionLimit (CES proxy); geothermal (P_Geothermal / EGS) funnel. | Our rows; emission-penalty and emission-limit machinery exists but is untested on NA data (needs one probe run); CCS retrofit = new technology (M). | YELLOW | All parameters exist. Two model-side items: (a) the CO2-price / emission-cap machinery has not been exercised on NA data (one 1924-probe run settles it), (b) the 12-year 45Q term and the retrofit-vs-new-build distinction need an approximation or a new retrofit technology. | High for credits, PPAs and project facts; the policy path (CO2 price, CES) is by definition a what-if | nuclear_announced / nuc_ccgtrelax. | 14A full: CO2 price $30 (2029) -> $60 (2035) -> $90/t (2040), RES/storage capex x0.7 from 2029, P_Gas_CCS 2/15/40 GW max with 45Q credit, nuclear minima (announced + 5 GW uprates + 5.4 GW hyperscaler SMR), state CES caps. 14B = 14A without the CO2 price. 14C stretch "net-zero power 2040": national power CO2 cap -50 % (2030) / -90 % (2040) vs 2025 (AnnualEmissionLimit), CCS retrofit technology on the existing CCGT fleet (capex +$1,100/kW, -7 pp efficiency, 90 % capture, 45Q), SMR as in 7A, geothermal/EGS unlocked (P_Geothermal max 5/20 GW 2035/40), RES funnel max x2, IC grid_high. | M-L | OBBBA/IRS 45Q; NETL Rev 3; OCED May 2025; Meta Jan 2026; DOE loans; Fervo Sep 2026; EO 14302/14300; DOE UPRISE; EIA state targets; IEA WEI 2026

## Assumptions
ID | Scenario | Variant | Parameter / lever | Region(s) | Years | Value | Unit | Basis / derivation | Source id(s) | Confidence | Invented?
1 | EV comeback | 1A | Power_BEVs (US total) | US 9 pools | 2030 / 2035 / 2040 | 146 / 408 / 624 | TWh | EIA AEO2026 reference purchased electricity for transportation (0.497/1.392/2.130 quads x 293.07); base to 2027, linear 2028-30. FEL base = 71/213/442. | EIA-AEO26 | High | No
1 | EV comeback | 1A | Regional split of the increment | US 9 pools | 2028-2040 | proportional to the FEL regional Power_BEVs path | share | No regional AEO split; keeps FEL geography. Cross-check: 2025 EV sales shares CA 23.9 %, CO 19.9, WA 19.0, NJ 12.2, NY 9.1, TX 7.1, US 9.6 %. | AAI-25 | Medium | Partly (method)
1 | EV comeback | 1A | Power_BEVs Canada | Canada | 2030 / 2035 / 2040 | 29 / 72 / 125 | TWh | CER EF2026 net-zero transport electricity (Current Measures 13/29/45; FEL base 14/37/62). EVAS repealed Feb 2026 -> upside only if targets become binding. | CER-EF26 | Medium | No
1 | EV comeback | 1B | Commercial-vehicle share (LCV+MHDV+buses) multiplier on 1A | US 9 pools | 2030-2040 | x1.25 | factor | NREL EFS High electrifies 61 % MDV / 41 % HDV VMT by 2050 vs 29/10 % Medium; no 2040 number -> stylised. | NREL-EFS | Low | Partly
1 | EV comeback | context | BEV sales / stock (AEO2026) | US | 2030 / 2035 / 2040 | 6.0/8.8/9.0 M sales; 23.3/62.3/100.5 M stock | M vehicles | AEO2026 supplement tables 38/39; implied ~4,900-5,300 kWh per plug-in vehicle (all modes). | EIA-AEO26 | High | No
1 | EV comeback | context | Downside bracket | US | 2030 | 17 % EV share (BNEF EVO 2026), Q1-Q2 2026 BEV share 5.8 % | share | Context only: shows the base is between BNEF and AEO. | BNEF-EVO26; COX-26 | Medium | No
2 | H2 comeback | 2A | Power_Hydrogen (US total) | US 9 pools | 2028 / 2030 / 2035 / 2040 | 10 / 27 / 165 / 333 | TWh | 2030 = DOE firm electrolyser pipeline 3.8 GW x 80 % CF; 2035 = 3 Mt electrolytic, 2040 = 6 Mt (30 % of the DOE 20 Mt clean-H2 target) x 55.5 kWh/kg. | DOE-REC24001; DOE-H2STRAT; EIA-AEO26-HMM | Medium | Partly (30 % share)
2 | H2 comeback | 2A | Regional shares of Power_Hydrogen | ERCOT/PJM/MISO/California/SPP/WECC | 2028-2040 | 35 / 25 / 20 / 10 / 5 / 5 | % | Retained hubs: HyVelocity (TX), ARCH2 (WV/OH/PA) + MACH2 (PA/DE/NJ), MachH2 (IL/IN/MI) + Heartland (MN/ND/SD); ARCHES (CA) terminated but state-funded. | DOE-H2HUBS26 | Medium | Partly (shares)
2 | H2 comeback | 2A | Power_Hydrogen Canada | Canada | 2030 / 2035 / 2040 | 25 / 52 / 80 | TWh | CER EF2026 Current Measures electrolysis 0.45 -> 1.45 Mt x 55.5 kWh/kg (mostly NL/NS export projects). | CER-EF26 | Medium | No
2 | H2 comeback | 2B | All 2A demand rows | all | 2028-2040 | x0.5 | factor | Half case (15 % electrolytic share). | - | Low | Yes
2 | H2 comeback | context | Electrolyser economics | US | 2024-2031 | alkaline capex $2,000-2,600/kW (outside China); DOE PEM $2/kg 2026, $1/kg 2031; 45V requires construction start before 2028-01-01 | - | Policy-conditional trigger for 2A. | IEA-GHR25; DOE-H2PEM; IRS-45V | High | No
3 | Age of compute | 3A | Power_DataCenter (US total) | US 9 pools | 2030 / 2035 / 2040 | 726 / 1,450 / 2,230 | TWh | 2030 = FEL base; 2035 = BNEF 194 GW x 8.76 x 0.85 LF; 2040 = +9 %/yr (McKinsey 2030-40 CAGR 6-12 % midpoint). Regional split = FEL base shares. | BNEF-DC26; MCK-26 | Medium | Partly (2040 CAGR)
3 | Age of compute | 3A/3B | Crypto mining load (flat profile) | ERCOT 40 %, SPP 15, MISO 15, SERC 10, PJM 10, WECC 10 | 2026 / 2035 / 2040 | 60 / 80 / 80 | TWh | CCAF global 138 TWh (Jun 2026) x ~40 % US share; EIA 2024 range 25-91 TWh. Regional split from known mining locations. | CCAF-26; EIA-CRYPTO24 | Medium | Partly (split)
3 | Age of compute | 3A/3B | Robotics / dark factories load (flat) | industrial regions by FEL industry share | 2028 / 2035 / 2040 | 5 / 90 / 150 | TWh | Wood Mackenzie global 78 -> 363 TWh by 2035 x 25 % US share; 2040 extrapolated. | WM-ROBOT26 | Low | Partly (share, 2040)
3 | Age of compute | 3A/3B | Telecom/edge/6G + defense AI load (flat) | by load share | 2030 / 2040 | 10 / 50 | TWh | No published estimate; stated dial (x3 in 3C). | - | Low | Yes
3 | Age of compute | 3B | Power_DataCenter | US | 2035 / 2040 | 2,188 / 3,585 (existing dc_high) | TWh | Existing sensitivity; above published forecasts - the space a phase-two scenario explores. | FEL-DCHIGH | High | No
3 | Age of compute | context | External DC forecasts | US | 2028-2035 | LBNL ref 464 (2028) / 649 (2030), range 521-843; EPRI 380/550/790 (2030); McKinsey 81/96/114 GW (2030); S&P 134-183 GW (2030); Grid Strategies 90 GW DC peak by 2030; BNEF 194 GW (2035) | TWh / GW | Calibration of the base. | LBNL-26; EPRI-26; MCK-26; SP-26; GS-25; BNEF-DC26 | High | No
3 | Age of compute | context | Hyperscaler capex | global | 2025 / 2026 | ~$410 bn actual (big 4); 2026 guidance $660-725 bn (the "$600 bn" was Nov-2025 consensus) | USD | Context. | FUTURUM-26; GOLDMAN-26 | Medium | No
4 | Space race | 4B | Terrestrial space-industry load (flat) | ERCOT 0.5 GW, SERC 0.3 GW, California 0.2 GW | 2028 -> 2035 ramp | ~8 | TWh/yr at 2035 | Starbase 250 MW gas plant (2021 EA) + ASU/liquefaction; propellant ~5,000 t/launch -> ~1.7 GWh/launch (ASU ~0.4 kWh/kg LOX, liquefaction ~0.3 kWh/kg CH4) = 2 TWh/yr even at 1,000 launches; other sites not found. | SPACEX-S1; FAA-STARBASE; FAA-SLC37 | Low | Partly (site loads)
4 | Space race | 4A | Orbital compute displacement | US DC | 2035 / 2040 | -5 / -13 / -27 % of US DC load (existing trio) | share | Existing space_dc sensitivities (DC in space assumptions sheet: 26/65/200 GW US moved to orbit by 2040). | FEL-SPACEDC | Medium | No
4 | Space race | context | SpaceX scale | - | 2026-2030 | S-1 filed 20 May 2026, priced 11 Jun 2026 ~$1.77 tn; FAA 25 Starship/yr Starbase, 76/yr SLC-37; orbital AI satellites from 2028 (~100 kW each) | - | Signal verification. | SPACEX-S1; FAA-SLC37 | Medium | No
5 | Political brakes | 5A | Power_DataCenter increment multiplier (on base growth after 2026) | ERCOT 0.3 (to 2030) then 0.6; California 0.5; NewYork 0.5; NewEngland 0.5; PJM 0.7; MISO 0.7; SERC 0.7; WECC 0.8; SPP 0.9; Canada 1.0 | 2027-2040 | see regions | factor | ERCOT anchored on BNEF (8.25 GW adds through 2030 vs FEL +253 TWh -> ~0.25); NY EO 62; moratoria leaders CA 73, GA 66, FL 60, NJ 51, NC 50 jurisdictions; statewide bills in 14 states. | TXBNEF-26; NY-EO62; GATHER-26; DCW-26 | Medium | Partly (multipliers)
5 | Political brakes | 5A | US gas new-build cap (CCGT+OCGT+engines), GroupTotalAnnualMaxNewCapacity | US 9 pools (group) | 2027-2031 | 10 | GW/yr | 50 % of the IIR schedule of ~107 GW gas starts 2026-30 (~21 GW/yr); turbine slots into 2031 (GEV), lead times 5-7 yr (EPRI). | IIR-25; GEV-26; UD-25 | Medium | Partly (50 %)
5 | Political brakes | 5A | Gas guardrail minimum removed (no forced builds) | all US | 2027-2040 | TotalAnnualMinCapacity gas = residual only | - | Political brake = no obligation to build the announced pipeline. | - | High | No
5 | Political brakes | 5A | RES funnel max = announced pipeline (x1.0 instead of x1.3) | all US | 2027-2032 | x1.0 | factor | Local opposition applies to all technologies; Data Center Watch counts DC only. | DCW-26 | Low | Yes
5 | Political brakes | 5B | Brakes released | all | 2031+ demand, 2032+ gas cap | multipliers -> 1.0; cap lifted | - | Post-2028 swing variant. | - | Low | Yes
5 | Political brakes | context | Opposition metrics | US | 2025-2026 | Gallup 71 % oppose local AI DC (Mar 2026); $156 bn blocked/delayed 2025, $130 bn Q1 2026; 632 jurisdictions, 270 adopted moratoria; ERCOT pause 49.8 GW (~20 % of US pipeline) | - | Signal verification: Gallup 71 % not 70 %; Data Center Watch publishes no moratoria count (the 500+ figure is from GatherGov/Wells Fargo). | GALLUP-26; DCW-26; GATHER-26; TXBNEF-26 | High | No
6 | Hormuz | 6A | Gas_Export demand (NorthAmerica_gas scenario) | ERCOT/MISO/SERC LNG regions | 2027-2032 | 95 % of EIA liquefaction capacity (21.2 Bcf/d 2028, 28.7 Bcf/d 2029) + 5 Bcf/d additional FID wave online by 2032 | Bcf/d | US LNG ran at 17.4 Bcf/d 1H26 (+23 %); Gulf LNG -54 bcm 2026; cumulative 2026-30 loss ~140 bcm (IEA). | EIA-LNG26; IEA-GMR26 | Medium | Partly (extra 5 Bcf/d)
6 | Hormuz | 6A | Henry Hub fuel path (folded model) | all | 2026-2027 / 2027-2029 | +10 % / +$2/MMBtu | USD/MMBtu | Observed: IMF "HH increased by only ~10 %"; EIA STEO Sep 2026 HH $3.43/$3.28; no source gives an extended-closure HH path -> +$2 is a stress dial. | IMF-WEO26; EIA-STEO26 | Low | Partly (+$2)
6 | Hormuz | 6B | TechnologyDiscountRate (all techs) | all | 2026-2030 | 5.0 -> 6.5 % (+150 bp), back to 5 % by 2033 | % | OECD: central banks +50-75 bp; Fed hike Sep 2026; Fitch NA utilities "deteriorating" -> risk premium. | OECD-26; FED-26; FITCH-26 | Low | Partly
6 | Hormuz | 6B | Capex multiplier (all generation, storage, IC) | all | 2026 / 2028 / 2032 | x1.15 / x1.15 / x1.00 | factor | Analogues: gas turbines +195 % vs 2019 (to ~$600/kW 2027), CT in-service $562 -> $728-1,544/kW (2023-25); Li-ion packs +7 % in 2022. | WM-TURB; GRIDLAB-25; BNEF-BAT22 | Low | Partly
6 | Hormuz | 6B | IC growth cap | all | 2026-2030 | 0.75 %/yr (grid_low logic) | %/yr | Utility capex freeze proxy; ~60 % of solar / 50 % of battery projects delayed early 2026. | FITCH-26; FEL-GRIDLOW | Low | Partly
6 | Hormuz | 6B | Demand | all | 2026-2030 | recession FEL (existing) then return to base by 2033 | - | Dallas Fed: 15 % disruption cuts US GDP growth 0.3 pp; 3-quarter closure +1.1 pp PCE; historical: 1974 -0.4 %, 1982 -2.8 %, 2009 -3.7 % retail sales. | DALLASFED-26; EIA-MER | Medium | No
6 | Hormuz | context | Scenario anchors | global | 2026 | WoodMac extended disruption: Brent ~$200, >11 mb/d shut in, TTF ~$14; Dallas Fed: WTI $115 Q3/$132 Q4 for 3-quarter closure; TTF/JKM $16-24 in 2026 | - | Signal verification: IEA "largest supply disruption in history" confirmed. | WM-HORMUZ26; DALLASFED-26; IEA-OMR26 | High | No
7 | Tech breakthrough | 7A | P_Nuclear_SMR TotalAnnualMaxCapacity (US+Canada total) | SERC 6, ERCOT 5, PJM 4, WECC 4, MISO 3, Canada 1.2 (2035 split); scaled for other years | 2030 / 2032 / 2035 / 2040 | 2 / 5 / 15 / 40 | GW | Projects with COD <= 2032: Darlington 300 MW (2030), Natrium 345 MW (2030-31), Clinch River 300 MW (2032), Hermes 2 50 MW (2030); deals: TVA/ENTRA1 up to 6 GW, Meta 4 GW SMR by 2035, Google 500 MW, Amazon up to 5 GW mid-2030s. Base: 0 / 0 / 2.9 / 18.7 GW. | OPG-25; TVA-26; TERRAPOWER-26; META-26; NUSCALE-25 | Medium | Partly (2040)
7 | Tech breakthrough | 7A | P_Nuclear_SMR CapitalCost | all | 2030 / 2035 / 2040 | 5,090 / 3,980 / 3,330 | EUR/kW | INL "Advanced" BOAK $5,500/kW (2030) with 9.5 % learning to the DOE Liftoff NOAK ~$3,600/kW by 2040; x0.925 EUR/USD. Base 9,091 flat. Bracket: INL Moderate $8,000 -> $4,000 (2050). | INL-ATB25; DOE-LIFTOFF24 | Medium | No
7 | Tech breakthrough | 7B | New storage S_/D_IronAir: E2P, RTE, life | all | from 2028 | 100 h; 45 %; 20 yr | - | Form Energy product (100 h); RTE 40-50 % (secondary sources). | FORM-26 | Medium | No
7 | Tech breakthrough | 7B | IronAir energy capex | all | 2028 / 2035 / 2040 | 60 / 30 / 20 | USD/kWh | Implied ~$77/kWh today (Eos backlog ~$237/kWh for comparison), Form target $20/kWh; timing of the glide path is an assumption. Unit conversion to the model storage capex convention to be checked. | FORM-26; EOS-26 | Low | Partly (timing)
7 | Tech breakthrough | 7B | IronAir power capex | all | 2028-2040 | ~300 | USD/kW | Backed out from DOE LDES Liftoff multi-day 2030 target ($1,100/kW system incl. energy). | DOE-LDES | Low | Partly
7 | Tech breakthrough | 7B | IronAir build limit (AnnualMaxNewCapacity, US) | US | 2028 / 2030 / 2032+ | 0.5 / 2 / 5 | GW/yr | Weirton plant 500 MW/yr by 2028; Google/Xcel 300 MW/30 GWh (MN, MISO) Feb 2026; pipeline 750 MW/75 GWh. | FORM-26 | Medium | Partly
7 | Tech breakthrough | 7C | Li-ion cost path | all | 2040 | x0.4 + 7 h duration (existing bess_optimistic) | - | Reuse; NREL ATB 2025 4 h $334 -> $147-339/kWh 2035 as the external bracket. | FEL-BESSOPT; NREL-ATB25 | High | No
7 | Tech breakthrough | 7C | P_Fusion (new, stylised) | PJM/WECC/SERC | 2035 / 2040 | max 2 / 10 GW; capex $12,300 (2035) -> $9,000/kW (2040); CF 0.85; no fuel cost | GW, USD/kW | CFS ARC ~400 MW VA early 2030s, county approval > $2.5 bn; Helion 50 MW slipping to 2030; peer-reviewed FOAK $1,400-43,000/kW -> use Lazard large-nuclear capex as the placeholder. | CFS-26; HELION-26; NATURE-FUSION26; LAZARD-26 | Low | Yes (caps, path)
7 | Tech breakthrough | metric | Gas displacement KPI | US | 2030-2040 | new gas GW vs base; EIA 2026 additions: batteries 24 GW vs gas 6.3 GW | GW | Report as the SE-relevant output. | EIA-ADD26 | High | No
8 | Canada DC frontier | 8A | Power_DataCenter Canada | Canada | 2030 / 2035 / 2040 | 41 / 130 / 220 | TWh | 2030 = ISED "5.5 GW needed by 2030" x 8.76 x 0.85; 2035 = ~16 GW (Alberta interim 1.2 + viable 4.8 + interruptible 1.6 + Meta 1.8 + ON/QC/BC ~2.5, plus growth); 2040 = ~28 GW trend. FEL base 71/178/269. | ISED-26; AESO-25; AESO-26; META-AB26; IESO-25; HQ-26 | Medium | Partly (2035/40)
8 | Canada DC frontier | 8A | P_Gas_CCGT Canada TotalAnnualMinCapacity increment (BYOP) | Canada | 2028 / 2030 / 2033 | +0.25 / +0.93 / +1.4 | GW | Capital Power bridge 250 MW (2H 2028); Greenlight 932 MW CCGT FID Jul 2026 COD 2H 2030 (permitted 1,864 MW); Wonder Valley phase 1 1.4 GW off-grid gas (unfinanced). | GREENLIGHT-26; WONDER-25 | Medium | Partly (Wonder Valley)
8 | Canada DC frontier | 8B | Power_DataCenter Canada | Canada | 2040 | 269 (FEL base) | TWh | FEL base path (above the announced pipeline); 8C goes beyond it. | FEL-BASE | High | No
8 | Canada DC frontier | context | Pipeline facts | Canada | 2026 | 337 MW AI DC operating; > 20 GW pipeline (18 GW Alberta); AESO Phase 2: 33 proposals / 20.7 GW, 4.8 GW viable; IESO DC 2.5 TWh 2026 -> 14 TWh 2050; Quebec 200 MW -> > 1 GW 2035; BC 400 MW cap 2026-28 | - | Signal verification: the C$13 bn campus is Meta Sturgeon County (1 -> 1.8 GW). | ISED-26; AESO-26; IESO-25; HQ-26; BCH-26 | High | No
9 | Water boom | 9A | Desalination load ERCOT (flat) | ERCOT | 2029 -> 2032 | 0.63 | TWh/yr | Corpus Christi 30 MGD + Harbor Island 100 MGD = 0.49 Mm3/d x 3.5 kWh/m3. | TXTRIB-26; ICN-26; NREL-WATER22 | Medium | No
9 | Water boom | 9A | Desal + reuse load California (flat) | California | 2028 -> 2040 | 0.5 | TWh/yr | Doheny 5 MGD SWRO (3.5 kWh/m3) + Pure Water SoCal 150 MGD + Pure Water LA 230 MGD reuse (0.84 kWh/m3). | MWD-25; LADWP-25; SCWD-26; NREL-WATER22 | Medium | No
9 | Water boom | 9A | Gulf-of-California desal + conveyance + Phoenix reuse (flat) | WECC (Arizona) | 2033 -> 2040 | 2.5 | TWh/yr | IDE-type 300 kAF/yr = 1.0 Mm3/d x (3.5 + 3.0 conveyance) kWh/m3 + ~100 MGD AWP x 0.84; WIFA earliest water 2031. | KJZZ-25; ENR-AZ; AZCT-25; ACEEE-06 | Low | Partly (conveyance)
9 | Water boom | 9B | All 9A rows | ERCOT/California/WECC | 2030-2040 | x10 (~37 TWh 2040) | factor | Boom multiplier; Texas Water Fund $20 bn 2027-47 and Colorado River 1.25 MAF/yr cuts as motivation. | TWF-25; USBR-26 | Low | Yes
9 | Water boom | context | Energy intensities | - | - | SWRO fleet 3.2 (1.6-4.8), Carlsbad 3.57; brackish 0.4-1.2; RO reuse 0.84; conveyance up to 3.6 (SWP) | kWh/m3 | Benchmarks. | NREL-WATER22; CARLSBAD; ACEEE-06 | High | No
10 | Climate relocation | 10A | Power_General re-allocation | from SERC+ERCOT+California to MISO/PJM/NewEngland/NewYork/WECC (by base load) | 2035 / 2040 | 2 % / 4 % of donor General load | share | No regional projection exists; First Street: 55 M movers by 2055, gainers ND/MT; Census 2025 shows the opposite flow today. | FIRST-25; CENSUS-26 | Low | Yes
10 | Climate relocation | 10A/10B | Cooling uplift on Power_General | SERC/ERCOT/SPP/California | 2040 | +3 % | share | CDD +10-80 % across NA (Nature Comm 2026); cooling ~15-20 % of Sunbelt load x ~+15 % CDD. | NATCOMM-26 | Low | Partly
10 | Climate relocation | 10A/10B | TradeCapacityGrowthCosts uplift (coastal) | SERC/ERCOT/NewYork/NewEngland corridors | 2027-2040 | x1.25 | factor | Hardening spend: Duke Florida $16 bn 5-yr plan, Entergy $15 bn/10 yr; distribution-side, proxied on IC. | DUKE-25; ENTERGY-22 | Low | Partly
10 | Climate relocation | context | Disaster statistics | US | 2023-2025 | 2025: 23 events, $115 bn, 276 deaths (LA fires $61.2 bn); 2024: 27; 2023: 28; H1 2025: 14 events | - | Signal correction: "15 in H1 2025" -> 14 (Climate Central continues the NOAA series). | CC-26 | High | No
11 | FEOC / BPS | 11A | Li-ion capex multiplier (D_ and S_) | all | 2026 / 2028 / 2030 / 2035 | x1.44 / x1.30 / x1.15 / x1.05 | factor | BNEF Dec 2025: North America packs +44 % vs global ($108 global, stationary $70); decay as domestic cells reach ~140 GWh/yr by 2028. | BNEF-BAT25; ACP-26 | Medium | Partly (decay)
11 | FEOC / BPS | 11A | PV capex multiplier (inverters) | all | 2026-2030 | x1.02 | factor | WoodMac: western inverter premium ~2 % of project capex; > 100 GWac US inverter capacity by end-2027. | WM-INV26 | Medium | No
11 | FEOC / BPS | 11A | TradeCapacityGrowthCosts multiplier (transformers) | all | 2026-2030 / 2035 | x1.30 / x1.10 | factor | Transformer prices +77 % (power) / +45 % (GSU) since 2019, lead times 128-144 weeks; ~40 % transformer share of IC capex assumed. | WM-TRAFO; INDSAGE-26 | Low | Partly (share)
11 | FEOC / BPS | 11A | Li-ion AnnualMaxNewCapacity (US) | US | 2026-2027 | 17 | GW/yr | WoodMac/ACP: 2026 installs below 2025 (18.9 GW / 51 GWh) for lack of FEOC-compliant BESS. | WM-ESM26 | Medium | No
11 | FEOC / BPS | 11B | Li-ion multiplier persists | all | 2030-2040 | x1.15 | factor | No-decay bracket. | - | Low | Yes
11 | FEOC / BPS | context | Policy facts | US | 2026-2031 | EO 14421 (26 Aug 2026), DOE rules ~Dec 2026; FEOC MACR storage 55/60/65/70/75 % (2026-30); tariff stack on CN ESS ~25 % (301) + 15 % (122); domestic modules 75 -> 180 GWh, cells 20 -> 140 GWh (2028); transformer plants ~$2 bn (Hitachi VA, Hyundai AL, Prolec NC, Siemens Energy NC, VanTran TX) | - | Signal correction: order number is 14421, not 14420. | EO-14421; BAKERTILLY; GATEWAY-26; ACP-26; IIR-26 | High | No
12 | AI overbuild | 12A | Power_DataCenter (US total) | US 9 pools | 2030 / 2035 / 2040 | 540 / 620 / 690 | TWh | 2030 = Grid Strategies -25 GW (-40 %) on utility DC forecasts ~ LBNL low case 521 TWh; +2 %/yr after 2030 (assumption). Regional split = FEL base shares. | GS-25; LBNL-26 | Medium | Partly (post-2030)
12 | AI overbuild | 12B | Power_DataCenter | US | 2030 / 2035 / 2040 | 369 / 805 / 874 (existing dc_low) | TWh | Existing sensitivity as the deep bracket. | FEL-DCLOW | High | No
12 | AI overbuild | context | Realisation evidence | US | 2025-2026 | WoodMac: 298 of 1,066 GW requested committed (28 %); Bernstein 135 of 492 GW credible; 5-10x duplicate requests; Exelon -40 %, AEP Ohio -50 %, PJM -43 % forecast cuts; ~4 GW under construction vs 12 GW planned 2026 (Sightline) | - | Context. | WM-DC26; BERNSTEIN-26; SIGHTLINE-26 | Medium | No
13 | Reindustrialization | 13A | Semiconductor fab load (flat) | WECC (AZ+ID): 9.5/22/25; NewYork: 0/6/13; ERCOT: 6/13/13; PJM (OH): 0/3/6 | 2030 / 2035 / 2040 | see regions | TWh/yr | ~3 MWh/wafer (TSMC 37.1 kWh per 12-inch wafer mask layer x ~80 layers) x 100k wafers/month = 3.6 TWh/yr (~400 MW) per fab; TSMC AZ 3 -> 6 fabs, Micron Boise 2, Micron Clay 2 -> 4, Samsung Taylor 2, TI Sherman 2, Intel OH 1 -> 2 (2031+). | TSMC-AR24; MICRON-26; TSMC-AZ; INTEL-OH | Medium | Partly (layers, fab size, timing)
13 | Reindustrialization | 13A | Primary aluminium smelter (flat) | SPP (Oklahoma) | 2030 -> 2040 | 10.7 | TWh/yr | Century/EGA Inola 750 kt/yr x ~14.3 MWh/t (IAI world average; PSO power deal pending); construction from end-2026, production ~2030. | CENTURY-26; IAI | Medium | No
13 | Reindustrialization | 13A | ERCOT non-DC large loads (industrial, H2, crypto excluded) | ERCOT | 2028 -> 2035 | 30 (2030) / 79 (2035+) | TWh/yr | ~10 % of the 474 GW queue (~45 GW) x 25 % realisation x 8.76 x 0.8 LF; WoodMac: 28 % of requests committed nationally. | RTOI-26; ERCOT-26; WM-DC26 | Low | Partly (realisation)
13 | Reindustrialization | 13A | Steel EAF/DRI, battery, defense, minerals (flat) | MISO 3/6/8; SERC 3/6/8 | 2030 / 2035 / 2040 | see regions | TWh/yr | Stylised adder for Nucor WV, SDI MS, Hybar AR, lithium AR, shipyards; individual MW not researched (dial; doubled in 13B, expanded in 13C). | - | Low | Yes
13 | Reindustrialization | 13A | Total adder | US | 2030 / 2035 / 2040 | +62 / +146 / +165 | TWh | Sum of the rows above; compare AEO2026 industrial electricity 1,059 -> 1,162 TWh (+103 TWh by 2040) as the reference-case envelope. | EIA-AEO26 | Medium | Partly
13 | Reindustrialization | 13B | Queue realisation 50 % and doubled placeholder adders | ERCOT/MISO/SERC | 2030-2040 | ~+230 TWh by 2040 | TWh | High bracket. | - | Low | Yes
14 | Decarb re-accelerates | 14A | Par_EmissionsPenalty CO2 price | all US (Canada optional) | 2029 / 2035 / 2040 | 30 / 60 / 90 | USD/t | Policy assumption; anchored on 45Q $85/t as the revealed federal CO2 value; base has no price. | IRS-45Q | Low | Partly (path)
14 | Decarb re-accelerates | 14A/14B | RES + storage capex multiplier (restored 30 % ITC) | all US | 2029-2040 | x0.70 | factor | 45Y/48E for wind/solar end for projects placed in service after 2027 unless construction began by Jul 2026; swing = restoration. | OBBBA-CREDITS | Medium | No
14 | Decarb re-accelerates | 14A/14B | P_Gas_CCS TotalAnnualMaxCapacity (US) | SERC/ERCOT/PJM/MISO/California | 2030 / 2035 / 2040 | 2 / 15 / 40 | GW | Base = 0 (disabled). Anchors: Sutter 550 MW, Baytown 810 MW as FOAK CCPP+CCUS; capex 2,593 EUR/kW in the data vs NETL 90 % capture TOC $2,049/kW (2018$). | NETL-23; OCED-25 | Low | Partly (caps)
14 | Decarb re-accelerates | 14A/14B | 45Q credit as negative VariableCost for CCS techs | all US | 2029-2040 | -8.5 (equiv. ~30 EUR/MWh el) | M EUR per PJ electricity | $85/t x 90 % capture x 56.1 kt CO2 per PJ gas x (1/0.47 el efficiency) x 0.925; 12-year term approximated by applying 2029-2040 to plants built <= 2033. | IRS-45Q; NETL-23 | Medium | Partly (term)
14 | Decarb re-accelerates | 14A/14B | Nuclear minima (TotalAnnualMinCapacity increments) | US by project region | 2027-2035 | nuclear_announced (+19.1 GW by 2035) + uprates +2.5 GW 2027 / +5 GW 2029 + hyperscaler SMR 5.4 GW 2030-35 | GW | Existing scenario + DOE UPRISE + Meta/Google/Amazon SMR deals (trackers: 9.8 GW in 13 deals incl. 1.4 GW restarts already in the fleet). | FEL-NUCANN; DOE-UPRISE26; META-26; NUC-TRACKER26 | Medium | No
14 | Decarb re-accelerates | 14A | Par_RegionalAnnualEmissionLimit (power CO2 vs 2025) | NewYork -80 %; NewEngland -70 %; California -60 %; PJM -40 % | 2040 (linear from 2029) | see regions | % reduction | Proxy for state 100 % targets (NY 2040, CT 2040, NJ 2035, CA 2045, VA 2045/50); PJM partial (NJ/MD/VA/IL). | EIA-100PCT | Low | Partly (shares)
14 | Decarb re-accelerates | context | Corporate CFE facts | US | 2026 | Meta up to 6.6 GW nuclear by 2035 (Vistra 2.1 GW + 433 MW uprates, Oklo 1.2 GW from 2030, TerraPower 2.8 GW first 690 MW 2032); Crane 835 MW restart 2027 ($1 bn DOE loan); Duane Arnold 615 MW 2029; Google-Kairos 500 MW; Amazon-X-energy up to 5 GW; Fervo Cape Station 500 MW (Google 396 MW PPA); IEA WEI 2026 clean $2.2 tn | - | Signal verification. | META-26; DOE-LOANS26; FERVO-26; IEA-WEI26 | High | No
1 | EV comeback | 1C stretch | Power_BEVs (US total) | US 9 pools | 2030 / 2035 / 2040 | 190 / 550 / 850 | TWh | EEI 2024 pre-OBBBA path (7.7 M/46 % sales 2030, 12.2 M/72 % 2035, stock 78.5 M 2035 = 1.26x AEO2026 stock) applied to the AEO2026 TWh path; 2040 extrapolated. | EEI-24; EIA-AEO26 | Medium | Partly (2040)
2 | H2 comeback | 2C stretch | Power_Hydrogen (US total) | US hub regions (2A shares) | 2030 / 2035 / 2040 | 40 / 280 / 555 | TWh | 10 Mt electrolytic by 2040 = 50 % of the DOE 20 Mt target x 55.5 kWh/kg; 2035 = 5 Mt. | DOE-H2STRAT; EIA-AEO26-HMM | Low | Partly (share)
2 | H2 comeback | 2C stretch | Power_Hydrogen Canada | Canada | 2040 | 165 | TWh | CER EF2026 net-zero electrolysis 3.0 Mt x 55.5 kWh/kg. | CER-EF26 | Medium | No
3 | Age of compute | 3C stretch | Second-wave adders x3 on dc_high | US by 3A splits | 2035 / 2040 | crypto 200 / robotics 300->450 / telecom-defense 80->150 | TWh | 3A adders tripled; DC = dc_high (2,188/3,585) with funnel caps lifted (dc_high_limitless logic). | FEL-DCHIGH; FEL-DCHL | Low | Yes
4 | Space race | 4C stretch | E-propellant electricity (flat) | ERCOT 50 %, California 20 %, SERC 20 %, WECC 10 % | 2030 / 2035 / 2040 | 2 / 20 / 100 | TWh | Synthetic CH4 for Starship: 1,000 t CH4/launch = 250 t H2 (55 kWh/kg = 13.8 GWh) + 2,750 t CO2 by DAC (~2 MWh/t = 5.5 GWh) + liquefaction/ASU (~1.7 GWh) ~ 21 GWh/launch; 100 / 1,000 / 5,000 launches per year. | SPACEX-S1; FAA-SLC37; DOE-H2PEM; NASEM-DAC | Low | Partly (launch counts)
4 | Space race | 4C stretch | Space manufacturing + ground segment (flat) | ERCOT/California/SERC/WECC | 2030 / 2035 / 2040 | 3 / 15 / 55 | TWh | Satellite, launcher and orbital-compute hardware factories (10 -> 40 TWh) + ground stations/ops (5 -> 15 TWh); no published basis, dial. | - | Low | Yes
4 | Space race | 4C stretch | Orbital compute displacement | US DC | 2040 | -27 % (space_dc_spacex) applied on top | share | Combined with the existing spacex case. | FEL-SPACEDC | Medium | No
5 | Political brakes | 5C stretch | Power_DataCenter (US+Canada) | all | 2027-2032 / 2033-2040 | frozen at the 2027 level / +3 %/yr | TWh | National moratorium what-if. | - | Low | Yes
5 | Political brakes | 5C stretch | Gas new-build cap; no new fossil permits | US (group) / NewYork, NewEngland, California | 2027-2035 | 5 GW/yr; gas+coal max = residual | GW/yr | Half of 5A cap; state permit bans as max = residual. | - | Low | Yes
6 | Hormuz | 6D stretch | HH fuel path / discount rate / capex / IC / demand | all | 2026-2032 | HH +$4/MMBtu 2027-31; WACC +300 bp 2026-32; capex +30 % 2026-29 -> 0 by 2034; IC growth 0 2026-30; recession demand through 2032; + EV 1A coupling | - | 1970s-style shock: Dallas Fed 1980 analogue (-5.6 pp GDP for a 15 % disruption then vs -0.3 pp now) motivates the harsher settings. | DALLASFED-26; EIA-MER | Low | Yes
7 | Tech breakthrough | 7C / 7D | P_Fusion CapitalCost | all | 2033 / 2035 / 2040 | USER INPUT (SE estimate) - central / low | USD/kW | Placeholder for the user-provided capex path; context only: CFS ARC county filing > $2.5 bn for ~400 MW; Tang et al. FOAK range $1,400-43,000/kW; Lazard large nuclear $12,300-17,570/kW. | USER; CFS-26; NATURE-FUSION26; LAZARD-26 | - | User input
7 | Tech breakthrough | 7C / 7D | P_Fusion FixedCost, VariableCost | all | 2033-2040 | USER INPUT; proposed default FOM 3 % of capex/yr, VOM 5 USD/MWh, fuel 0 | USD/kW-yr, USD/MWh | Defaults if the user has no FOM figure. | USER | - | User input
7 | Tech breakthrough | 7C / 7D | P_Fusion technical parameters | all | from first commercial year | CF 0.85; OperationalLife 30 yr; ramping as nuclear; CO2 0; first commercial year USER INPUT (default 2033) | - | Proposed defaults (CFS ARC early 2030s, Helion 2028-30 for 50 MW). | CFS-26; HELION-26 | Medium | Partly (defaults)
7 | Tech breakthrough | 7C | P_Fusion TotalAnnualMaxCapacity | PJM (VA) 40 %, WECC (WA) 20 %, SERC (TN) 20 %, California/ERCOT 20 % | 2035 / 2040 | 2 / 10 | GW | Announced sites: CFS Chesterfield VA, Helion Malaga WA, Type One/TVA TN, Pacific Fusion CA; dial. | CFS-26; HELION-26 | Low | Partly
7 | Tech breakthrough | 7D stretch | P_Fusion TotalAnnualMaxCapacity; capex | all | 2035 / 2040 | 5 / 40 GW; 50 % of the user central capex | GW; factor | "Everything early" what-if. | USER | - | Yes
7 | Tech breakthrough | 7D stretch | P_Nuclear_SMR TotalAnnualMaxCapacity | all | 2032 / 2035 / 2040 | 10 / 40 / 100 | GW | 5x the 7A pipeline; INL advanced capex path. | INL-ATB25 | Low | Yes
7 | Tech breakthrough | 7D stretch | IronAir energy capex and build limit | all | 2030+ | $20/kWh from 2030; AnnualMaxNewCapacity unlimited | - | Form target reached early; no supply constraint. | FORM-26 | Low | Yes
7 | Tech breakthrough | 7D stretch | Li-ion (Na-ion) capex | all | 2035 | x0.3 vs base | factor | Beyond bess_optimistic (x0.4 by 2040). | FEL-BESSOPT | Low | Yes
8 | Canada DC frontier | 8C stretch | Power_DataCenter Canada | Canada | 2030 / 2035 / 2040 | 60 / 240 / 335 | TWh | All Alberta Phase-2 proposals (20.7 GW) + Wonder Valley 7.5 GW + ON/QC/BC 4 GW = 32 GW by 2035; 45 GW by 2040; x 8.76 x 0.85. | AESO-26; WONDER-25; IESO-25; HQ-26 | Low | Partly (2040)
8 | Canada DC frontier | 8C stretch | P_Gas_CCGT Canada minimum (BYOP) and Canada-US IC | Canada | 2030 / 2035 | +2 / +10 GW gas minimum; IC growth x2 (grid_high logic) | GW | Greenlight 1.86 GW permitted + Wonder Valley 1.4 GW phase 1 + further BYOP; AESO gas-only rule for the interruptible pool. | GREENLIGHT-26; WONDER-25; AESO-26 | Low | Partly
9 | Water boom | 9C stretch | Manufactured-water load (flat) | WECC 40 %, California 30 %, ERCOT 20 %, SERC 10 % | 2030 / 2035 / 2040 | 4 / 18 / 36 | TWh | 10 Mm3/d desal + conveyance (6.5 kWh/m3 = 24 TWh) + 2 Mm3/d Florida SWRO (5 TWh) + pumped imports replacing 50 % of the Colorado deficit (1.5 MAF/yr x 3.6 kWh/m3 = 6.7 TWh). Israel ~2 Mm3/d today, Gulf states ~20. | NREL-WATER22; ACEEE-06; USBR-26; IDRA-25 | Low | Partly (scale)
10 | Climate relocation | 10C stretch | Power_General + DC growth re-allocation | SERC/ERCOT/California -> MISO/PJM/NewEngland/NewYork/WECC-north | 2035 / 2040 | 10 % / 20 % of donor loads | share | Great-Reshuffle what-if. | FIRST-25 | Low | Yes
10 | Climate relocation | 10C stretch | Sunbelt cooling uplift; coastal IC cost; coastal plant availability; rebuild load; reserve requirement | SERC/ERCOT/SPP/California; SERC/ERCOT/NY/NE corridors | 2030-2040 | +8 %; x1.50; -5 pp AvailabilityFactor gas+nuclear coastal; +1 % national General 2030-40; +5 pp peaking reserve SERC/ERCOT | - | Storm-outage and rebuild what-if. | CC-26; DUKE-25 | Low | Yes
11 | FEOC / BPS | 11C stretch | Li-ion build cap; wind/solar capex; exogenous replacement programme | US | 2026-2028; 2026-2030; 2028-2035 | 12 GW/yr; x1.10; 80 % of installed Chinese-origin inverters/BESS/transformers replaced (capex reported outside the optimisation) | - | Rip-and-replace reading of EO 14421 (installed equipment in scope: monitor/replace/remove). | EO-14421; WM-TRAFO | Low | Yes
12 | AI overbuild | 12C stretch | Power_DataCenter (US) | US 9 pools (Canada same ratio) | 2028 / 2032 / 2040 | 400 / 300 / 500 | TWh | AI-winter what-if: peak 2028, capex bust, consolidation, slow recovery. | - | Low | Yes
13 | Reindustrialization | 13C stretch | FEL industry electrification high + defense + critical minerals | industrial regions | 2040 | +250 (electrification, +20 % industrial General) + 20 (defense/shipbuilding) + 30 (minerals refining SPP/WECC/SERC) | TWh | Industrial-superpower what-if on top of 13B (~+530 TWh total). | EIA-AEO26 | Low | Yes
14 | Decarb re-accelerates | 14C stretch | AnnualEmissionLimit (power CO2 vs 2025) | US (national) | 2030 / 2040 | -50 % / -90 % | % reduction | Net-zero-power-by-2040 what-if. | - | Low | Yes
14 | Decarb re-accelerates | 14C stretch | P_Gas_CCGT_CCS_Retrofit (new technology) | all US | from 2029 | capex +$1,100/kW on existing CCGT; -7 pp efficiency; 90 % capture; 45Q credit; max = existing CCGT fleet | - | NETL Rev 3 delta TOC ($2,049 - $952/kW) as the retrofit adder. | NETL-23; IRS-45Q | Medium | Partly
14 | Decarb re-accelerates | 14C stretch | Geothermal unlock; RES funnel; IC | all | 2035 / 2040 | P_Geothermal max 5 / 20 GW; RES funnel max x2; IC grid_high | - | Fervo Cape Station 500 MW, Google 396 MW PPA as the seed; funnel/IC from existing sensitivities. | FERVO-26; FEL-GRIDHIGH | Low | Partly

## Feasibility
ID | Scenario | Severity | Type | Concern | Workaround / proposal
1 | EVs come back with a vengeance | GREEN | data | Regional split of the increment is a method choice (FEL geography vs state registration shares). | Use FEL geography; ACC II tilt as an option.
1 | EVs come back with a vengeance | GREEN | data | DNV ETO NA 2025 "muted" baseline not parsed (PDF on disk). | Parse if the DNV comparison is wanted in the write-up.
2 | Hydrogen comes back with a vengeance | YELLOW | model | Flat profile for a flexible load (electrolysers follow cheap power). | Accept for the first run; add X_Electrolyser + storage if the capacity result is decision-relevant.
2 | Hydrogen comes back with a vengeance | GREEN | data | Electrolytic share of clean H2 (retained hubs are mostly gas+CCS) - a dial, carried as 2A/2B/2C. | State the share in the scenario name.
2 | Hydrogen comes back with a vengeance | GREEN | data | Canada volumes hinge on Atlantic export projects. | Note the dependency.
3 | The Age of Compute - AI is only phase one | GREEN | data | FEL base dc_scenario content unknown (may already include second-wave growth). | Ask the FEL team; scale adders relative to the answer.
3 | The Age of Compute - AI is only phase one | GREEN | data | Telecom/edge/defense electricity has no published estimate; the adder is a stated dial. | Keep as dial (10 -> 50 TWh; x3 in 3C).
4 | A space race is coming | GREEN | data | Site-specific MW for Starbase grid connection, ASU and Starfactory not published; e-propellant chain derived from stoichiometry (0.25 t H2 + 2.75 t CO2 per t CH4). | State the derivation; the launch count is the dial.
4 | A space race is coming | GREEN | model | Orbital compute sign: displacement vs new load. | Run 4C both with and without the orbital-compute reduction.
5 | Political brakes on build-out | GREEN | data | Regional multipliers are our construction; ERCOT is the only directly quantified policy-to-GW effect. | Present as dials; anchor ERCOT on BNEF.
5 | Political brakes on build-out | GREEN | data | Opposition-cancelled gas GW not found in aggregate; cap derived from turbine delivery capacity. | Sensitivity on the cap.
6 | A multi-year Strait of Hormuz problem | YELLOW | model | Utility rate/capex freezes and inflation are behaviours outside the model. | Represent as IC-growth cap, funnel-max haircut, WACC and capex dials; say so.
6 | A multi-year Strait of Hormuz problem | GREEN | data | No published HH path for an extended closure; +$2 / +$4 are dials. | Run the spread.
7 | A generation/storage technology breakthrough | YELLOW | model | Iron-air and fusion are new technologies: sets, filter files, cost/E2P rows, subsets; storage energy capex unit (Li-ion 964 M EUR/PJ in the data) must be reconciled with $/kWh before writing. | One-off data work (M); pattern exists (add_nuclear_smr.py).
7 | A generation/storage technology breakthrough | GREEN | data | Fusion capex, FOM and first-commercial year come from the user; other fusion parameters proposed as defaults. | Fill the USER INPUT rows.
7 | A generation/storage technology breakthrough | GREEN | data | Iron-air RTE and power-component cost are secondary/target figures. | Carry as dials.
8 | Canada is the next data-center frontier | GREEN | model | Single Canada node averages Alberta gas and Quebec hydro; BYOP gas can be forced but not tied to the DC site. | Force the CCGT minimum in Canada; note the averaging.
8 | Canada is the next data-center frontier | GREEN | data | FEL base Canada DC exceeds the announced pipeline; decide whether 8A (below base) is shown or the base is re-based. | Open question; 8C provides the above-base tailwind either way.
9 | Water scarcity triggers an artificial-water-production boom | GREEN | data | No NA 2030/2040 desal forecast in open sources; project list + multipliers instead. | Dials.
10 | Climate-driven relocation and rebuild | YELLOW | model | Cooling uplift goes on General (cooling not separable in the FEL data); hardening spend is distribution-side. | Use General; proxy hardening on IC cost; say so.
10 | Climate-driven relocation and rebuild | GREEN | data | Relocation shares and rebuild load are dials without an external regional projection. | Present as dials (10A/10C).
11 | FEOC restrictions on the Bulk-Power System | GREEN | model | Equipment origin is not a model dimension; replacement of installed gear must be an exogenous adder. | 11C reports it outside the optimisation.
11 | FEOC restrictions on the Bulk-Power System | GREEN | data | Decay of the premium as domestic capacity ramps is a dial. | 11A vs 11B.
12 | AI overbuild correction | GREEN | data | Post-2030 path after a correction is a dial. | 12A/12B/12C bracket.
13 | Reindustrialization / onshoring as an independent load engine | GREEN | data | Per-fab MW derived (layers x wafers), not disclosed. | State the derivation; cross-check with SRP/APS IRPs if available.
13 | Reindustrialization / onshoring as an independent load engine | GREEN | data | Possible overlap with FEL base industry growth. | Ask the FEL team; net out.
14 | Decarbonization re-accelerates | YELLOW | model | CO2 price / emission cap machinery untested on NA data. | One 1924 probe with a price and with a cap before the 49-hour runs.
14 | Decarbonization re-accelerates | YELLOW | model | 45Q is a 12-year per-plant credit; the model has annual VariableCost only; CCS retrofit is not a distinct technology. | Apply the credit 2029-2040; add P_Gas_CCGT_CCS_Retrofit (M).
14 | Decarbonization re-accelerates | GREEN | data | CO2 price level and CES shape are policy what-ifs. | 14A/14B/14C bracket.
14 | Decarbonization re-accelerates | GREEN | data | Nuclear ITC (40 %) may already be netted in LCOE v1.4 capex. | Confirm with the LCOE owner.

## Sources
Source id | Organisation | Title | Date | URL | Used for
EIA-AEO26 | U.S. EIA | Annual Energy Outlook 2026, reference case Tables 2, 8, 38, 39 (transport/industrial electricity, BEV sales/stock) | 2026-04-08 | https://www.eia.gov/outlooks/aeo/excel/aeotab2.xlsx ; https://www.eia.gov/outlooks/aeo/supplement/excel/suptab_38.xlsx | S1, S13
EIA-AEO26-HMM | U.S. EIA | AEO2026 Hydrogen Market Module assumptions (55.5 kWh/kg PEM, 80 % CF, 45V) | 2026-04 | https://www.eia.gov/outlooks/aeo/assumptions/ | S2
COX-26 | Cox Automotive / KBB | Q1 and Q2 2026 EV sales report commentary (BEV share 5.8 %) | 2026-04-10 / 2026-07-10 | https://www.coxautoinc.com/insights/q2-2026-ev-sales-report-commentary/ | S1
AAI-25 | Alliance for Automotive Innovation | Get Connected EV Quarterly Report Q4 2025 (state registration shares) | 2026-03-25 | https://www.autosinnovate.org/ | S1
CER-EF26 | Canada Energy Regulator | Canada's Energy Future 2026 (end-use demand CSV; transport electricity; electrolysis) | 2026 | https://www.cer-rec.gc.ca/en/data-analysis/canada-energy-future/ | S1, S2
BNEF-EVO26 | BloombergNEF (via Utility Dive) | Electric Vehicle Outlook 2026 (US share 2030 cut to 17 %) | 2026-06-16 | https://www.utilitydive.com/ | S1
NREL-EFS | NREL | Electrification Futures Study: Scenarios of electric technology adoption (Table 7.1) | 2018 | https://www.nrel.gov/docs/fy18osti/71500.pdf | S1
DOE-REC24001 | U.S. DOE | Hydrogen Program Record 24001: electrolyzer installations in the US (3.8 GW firm) | 2024-05 | https://www.hydrogen.energy.gov/docs/hydrogenprogramlibraries/pdfs/24001-electrolyzers-installed-in-us.pdf | S2
DOE-H2HUBS26 | DOE OCED / CATF / decarbonfuse | H2Hubs status 2026: five retained hubs (~$4.8 bn), ARCHES and PNWH2 terminated Oct 2025 | 2026-04 / 2026-05-11 | https://www.energy.gov/oced/regional-clean-hydrogen-hubs-0 | S2
DOE-H2STRAT | U.S. DOE | National Clean Hydrogen Strategy and Roadmap (10/20/50 Mt) | 2023-06 | https://www.hydrogen.energy.gov/library/roadmaps-vision/clean-hydrogen-strategy-roadmap | S2
DOE-H2PEM | U.S. DOE HFTO | Hydrogen Shot / PEM electrolyzer cost and efficiency targets | 2024-2026 | https://www.energy.gov/eere/fuelcells/hydrogen-shot | S2
IEA-GHR25 | IEA | Global Hydrogen Review 2025 (electrolyser capex, 45V Box 6.1) | 2025-09 | https://www.iea.org/reports/global-hydrogen-review-2025 | S2
IRS-45V | IRS / Treasury | 45V after OBBBA: begin construction before 2028-01-01 | 2025-07 | https://www.irs.gov/credits-deductions/clean-hydrogen-production-credit | S2
LBNL-26 | Lawrence Berkeley National Laboratory | 2025 United States Data Center Energy Usage Report - Update (2028: 464 TWh; 2030: 649 TWh, 521-843) | 2026-06 | https://eta.lbl.gov/publications/ | S3, S12
EPRI-26 | EPRI | Powering Intelligence 2026 (DC 380/550/790 TWh 2030) | 2026-03 | https://powering-intelligence.epri.com/ | S3
GS-25 | Grid Strategies | Strategic Industries Surging: 5-year load growth forecast (166 GW peak 2025-30; DC forecasts overstated ~25 GW) | 2025-11 | https://gridstrategiesllc.com/ | S3, S12
MCK-26 | McKinsey (NASEO energy outlook deck) | US power demand outlook 2026 (34 -> 81/96/114 GW DC 2030; ~70 % of growth to 2035) | 2026 | https://energyoutlook.naseo.org/ | S3
BNEF-DC26 | BloombergNEF (via Latitude Media / Utility Dive) | US data-center capacity outlook revised to 194 GW by 2035 | 2026-07 | https://www.latitudemedia.com/ | S3
SP-26 | S&P Global | US data-center power demand 75.8/108/134 GW 2026/28/30; opposition analysis | 2025-10 / 2026-01-29 | https://www.spglobal.com/ | S3, S5
FUTURUM-26 | Futurum / CNBC | Hyperscaler capex 2026 guidance $660-725 bn | 2026-02 / 2026-07 | https://futurumgroup.com/ | S3
GOLDMAN-26 | Goldman Sachs | Tracking Trillions: AI capex $765 bn 2026 -> $1.6 tn 2031 | 2026 | https://www.goldmansachs.com/insights/ | S3
CCAF-26 | Cambridge Centre for Alternative Finance | Cambridge Bitcoin Electricity Consumption Index (global 138 TWh, Jun 2026) | 2026-06 | https://ccaf.io/cbnsi/cbeci | S3
EIA-CRYPTO24 | U.S. EIA | Tracking electricity consumption from US cryptocurrency mining (25-91 TWh, 10.3 GW) | 2024-02 | https://www.eia.gov/todayinenergy/detail.php?id=61364 | S3
WM-ROBOT26 | Wood Mackenzie | Robotics electricity demand 78 -> 363 TWh by 2035 (global) | 2026-08 | https://www.woodmac.com/ | S3
FEL-DCHIGH | FEL 2026 / data repo | NorthAmerica_dc_high sensitivity (DC 2,188/3,585 TWh) | 2026-07 | data repo Par_SpecifiedAnnualDemand/NorthAmerica_dc_high | S3
FEL-DCLOW | FEL 2026 / data repo | NorthAmerica_dc_low sensitivity (DC 369/805/874 TWh) | 2026-07 | data repo Par_SpecifiedAnnualDemand/NorthAmerica_dc_low | S12
FEL-SPACEDC | SE internal | DC in space - assumptions sheet (GW moved to orbit: base/disruptive/SpaceX) | 2026-08 | NA_inputs/DC in space - assumptions sheet.xlsx | S4
SPACEX-S1 | SpaceX / SEC EDGAR | Form S-1 and S-1/A (CIK 1181412): capex, power supply constraints, orbital compute | 2026-05-20 / 2026-06-03 | https://www.sec.gov/cgi-bin/browse-edgar?action=getcompany&CIK=1181412 | S4
FAA-STARBASE | FAA | Starbase environmental assessment (250 MW gas plant; 25 launches/yr) | 2021-2022 | https://www.faa.gov/space/stakeholder_engagement/spacex_starship | S4
FAA-SLC37 | FAA | Record of Decision SLC-37 Starship (up to 76 launches/yr) | 2025-11-20 | https://www.faa.gov/space/stakeholder_engagement/spacex_starship_ccsfs | S4
GALLUP-26 | Gallup | Americans oppose AI data centers in their area (71 % oppose) | 2026-05-13 | https://news.gallup.com/poll/709772/ | S5
DCW-26 | Data Center Watch | 2025 Year in Review; Q1 2026 report ($156 bn / $130 bn blocked or delayed) | 2026-01 / 2026-04 | https://www.datacenterwatch.org/report | S5, S12
GATHER-26 | GatherGov via CRE Daily; Wells Fargo via ZeroHedge | Local data-center moratoria counts (632 jurisdictions with formal action; 374 active) | 2026-09-16 / 2026-09-09 | https://finance.yahoo.com/ | S5
NY-EO62 | Governor of New York | Executive Order 62 on hyperscale data centers (permits withheld pending GEIS); S.10462/A.11560 passed | 2026-07-14 | https://www.governor.ny.gov/ | S5
TXBNEF-26 | Utility Dive / BloombergNEF | Texas pause on ERCOT data-center interconnections (~49.8 GW); BNEF ~8.25 GW ERCOT DC adds through 2030 | 2026-08-06 | https://www.utilitydive.com/news/texas-data-center-pause-bnef/827185/ | S5
IIR-25 | Industrial Info Resources | ~107 GW of US gas-fired starts scheduled 2026-30 | 2025-09-15 | https://www.industrialinfo.com/ | S5
GEV-26 | GE Vernova (Turbomachinery Magazine) | Gas turbine backlog 116 GW; new orders deliver 2031 | 2026-07 | https://www.turbomachinerymag.com/view/ge-vernova-gas-turbine-backlog-hits-116-gw | S5, S6
UD-25 | Utility Dive (EPRI) | Gas turbine lead times 5-7 years | 2025-08-21 | https://www.utilitydive.com/ | S5
OBBBA-CREDITS | IRS Notice 2025-42 / Eide Bailly | 45Y/48E phase-out for wind/solar; storage credit schedule | 2025-08 | https://www.irs.gov/pub/irs-drop/n-25-42.pdf | S5, S14
WM-HORMUZ26 | Wood Mackenzie | Strait of Hormuz: Extended Disruption scenario (Brent ~$200, TTF ~$14) | 2026-05-20 | https://www.woodmac.com/ | S6
DALLASFED-26 | Federal Reserve Bank of Dallas | Hormuz closure scenarios: oil price, GDP and PCE effects | 2026-03-20 / 2026-04-17 / 2026-06-23 | https://www.dallasfed.org/research/economics/2026/ | S6
EIA-STEO26 | U.S. EIA | Short-Term Energy Outlook Jun-Sep 2026 (Brent, HH, LNG exports) | 2026-09 | https://www.eia.gov/outlooks/steo/ | S6
EIA-LNG26 | U.S. EIA | US liquefaction capacity and LNG export outlook (21.2 Bcf/d 2028; 28.7 Bcf/d 2029) | 2026 | https://www.eia.gov/naturalgas/ | S6
IMF-WEO26 | IMF | World Economic Outlook Update July 2026 (HH +10 %, LNG +50 % Asia) | 2026-07 | https://www.imf.org/en/Publications/WEO | S6
OECD-26 | OECD | Economic Outlook June 2026 (prolonged disruption scenario, +50-75 bp) | 2026-06 | https://www.oecd.org/en/publications/oecd-economic-outlook | S6
IEA-GMR26 | IEA | Gas Market Report Q3 2026 (TTF/JKM, Gulf LNG losses) | 2026-07 | https://www.iea.org/reports/gas-market-report-q3-2026 | S6
IEA-OMR26 | IEA | Oil Market Report April 2026 ("largest supply disruption in history") | 2026-04 | https://www.iea.org/reports/oil-market-report-april-2026 | S6
FED-26 | Federal Reserve | FOMC statement 16 Sep 2026 (+25 bp to 3.75-4.00 %) | 2026-09-16 | https://www.federalreserve.gov/ | S6
FITCH-26 | Fitch Ratings | North American utilities sector outlook revised to deteriorating | 2026-06-12 | https://www.fitchratings.com/ | S6
WM-TURB | Wood Mackenzie / East Daley | Gas turbine prices ~$600/kW by 2027 (+195 % vs 2019) | 2025-2026 | https://www.woodmac.com/ | S6
GRIDLAB-25 | GridLab | Combustion turbine in-service costs $562 (2023) -> $728-1,544/kW (2025) | 2025 | https://gridlab.org/ | S6
BNEF-BAT22 | BloombergNEF | Battery price survey 2022 (+7 % to $151/kWh) | 2022-12 | https://about.bnef.com/ | S6
EIA-MER | U.S. EIA | Monthly Energy Review Table 7.6 (retail sales history) | 2026 | https://www.eia.gov/totalenergy/data/monthly/ | S6
INL-ATB25 | Idaho National Laboratory / NREL ATB 2025 | Meta-analysis of advanced nuclear cost estimates (SMR $5,500/8,000/10,000 per kW BOAK; 9.5 % learning) | 2025 | https://atb.nrel.gov/electricity/2025/nuclear | S7
DOE-LIFTOFF24 | U.S. DOE | Pathways to Commercial Liftoff: Advanced Nuclear (FOAK $6,000-10,000/kW; NOAK ~40 % lower) | 2024-09 | https://liftoff.energy.gov/advanced-nuclear/ | S7
OPG-25 | Ontario Power Generation / WNN | Darlington 4 x BWRX-300: C$20.9 bn, unit 1 end-2030 | 2025-05 | https://www.world-nuclear-news.org/ | S7, S14
TVA-26 | TVA / ANS | Clinch River BWRX-300 (~$5.4 bn first unit; COD 2032); NRC construction permit process | 2026-07 | https://www.ans.org/news/ | S7, S14
TERRAPOWER-26 | TerraPower / ANS | Natrium Kemmerer construction permit Mar 2026; COD 2030-31; ~$4 bn | 2026-04 | https://www.terrapower.com/ | S7
NUSCALE-25 | NuScale / ENTRA1 / TVA (ANS) | Up to 6 GW SMR framework agreement | 2025-09-03 | https://www.ans.org/news/ | S7
FORM-26 | Form Energy | Google/Xcel 300 MW / 30 GWh (MN); Weirton 500 MW/yr by 2028; $20/kWh target; pipeline 750 MW / 75 GWh | 2026-02 / 2026-04 | https://formenergy.com/newsroom/ | S7
EOS-26 | Eos Energy (SEC 8-K) | Backlog $807 M / 3.4 GWh (~$237/kWh) | 2026-08-05 | https://www.sec.gov/ | S7
DOE-LDES | U.S. DOE | Pathways to Commercial Liftoff: Long Duration Energy Storage (2030 targets $650/kW inter-day, $1,100/kW multi-day) | 2023-03 | https://liftoff.energy.gov/long-duration-energy-storage/ | S7
NREL-ATB25 | NREL | Annual Technology Baseline 2025 - utility-scale battery storage costs | 2025 | https://atb.nrel.gov/electricity/2025/utility-scale_battery_storage | S7
LAZARD-26 | Lazard | LCOE+ 2026 (v19): nuclear $12,300-17,570/kW; CCGT $1,450-2,100/kW (post-2028 quotes $2,400-2,600) | 2026-06 | https://www.lazard.com/research-insights/levelized-cost-of-energyplus/ | S7
CFS-26 | Commonwealth Fusion Systems | ARC Chesterfield VA (~400 MW, early 2030s; Google 200 MW; Eni PPA) | 2025-2026 | https://cfs.energy/ | S7
HELION-26 | Helion (Axios) | Orion 50 MW for Microsoft; full capacity may slip to 2030 | 2026-09-08 | https://www.axios.com/ | S7
NATURE-FUSION26 | Tang et al., Nature Energy | Fusion FOAK capex $1,400-43,000/kW; experience rates 2-8 % | 2026 | https://www.nature.com/nenergy/ | S7
EIA-ADD26 | U.S. EIA | Planned 2026 capacity additions (86 GW: solar 43.4, battery 24, wind 11.8, gas 6.3) | 2026-02 | https://www.eia.gov/todayinenergy/ | S7
FEL-BESSOPT | FEL 2026 / data repo | NorthAmerica_bess_optimistic sensitivity | 2026-07 | data repo Par_X/NorthAmerica_bess_optimistic | S7
META-AB26 | Meta / Government of Alberta | Sturgeon Data Centre: 1 -> 1.8 GW, > C$13 bn | 2026-07-08 | https://www.alberta.ca/ | S8
GREENLIGHT-26 | Pembina / Kineticor / Morgan Stanley Infrastructure | Greenlight Electricity Centre 932 MW CCGT FID; COD 2H 2030; 250 MW bridge 2028 | 2026-07-02 | https://www.pembina.com/ | S8
AESO-25 | AESO | Large-load interim connection process (1,200 MW to 2028) | 2025-06 | https://www.aeso.ca/ | S8
AESO-26 | AESO / The Logic | Phase 2 large-load framework: 33 proposals / 20.7 GW, 4.8 GW viable, 1.6 GW interruptible pool | 2026-06 / 2026-08 | https://thelogic.co/ | S8
WONDER-25 | Wonder Valley / O'Leary Ventures | 7.5 GW / C$70 bn Greenview campus, phase 1 1.4 GW off-grid gas | 2025 | https://wondervalley.com/ | S8
ISED-26 | Innovation, Science and Economic Development Canada | AI data-centre deck: 337 MW operating, > 20 GW pipeline, 5.5 GW needed by 2030 | 2026-01 | https://ised-isde.canada.ca/ | S8
IESO-25 | IESO | 2025 Annual Planning Outlook (DC 2.5 TWh 2026 -> 14 TWh 2050) | 2025 | https://www.ieso.ca/ | S8
HQ-26 | Hydro-Quebec | Data-centre allocation 200 MW -> > 1 GW by 2035; 13 c/kWh tariff | 2026-02 | https://www.hydroquebec.com/ | S8
BCH-26 | BC Hydro | Data-centre cap 400 MW 2026-28 | 2026 | https://www.bchydro.com/ | S8
USBR-26 | US Bureau of Reclamation / DOI | Post-2026 Colorado River ROD; 2027-28 operations (1.25 MAF/yr mandatory cuts) | 2026-08-21 | https://www.usbr.gov/newsroom/news-release/5392 | S9
TXTRIB-26 | Texas Tribune | Corpus Christi desalination plant back on the agenda (30 MGD, ~$979 M) | 2026-06-01 | https://www.texastribune.org/2026/06/01/texas-corpus-christi-water-desalination-plant-returns/ | S9
ICN-26 | Inside Climate News | Nueces River Authority Harbor Island 100 MGD desalination (first water 2029) | 2026-06-22 | https://insideclimatenews.org/news/22062026/ | S9
MWD-25 | Metropolitan Water District of Southern California | Pure Water Southern California cost update (115 -> 150 MGD; $8.3 bn) | 2025-09-23 | https://www.mwdh2o.com/building-local-supplies/pure-water-southern-california/ | S9
LADWP-25 | LADWP / Brown and Caldwell | Pure Water Los Angeles (Hyperion, up to 230 MGD by 2035) | 2025-10 | https://www.ladwp.com/strategic-initiatives/pure-water-los-angeles | S9
SCWD-26 | South Coast Water District | Doheny Ocean Desalination (5 MGD, ops 2028) | 2026-03 | https://scwd.org/ | S9
KJZZ-25 | KJZZ | WIFA approves desalination pre-development proposals (earliest water 2031) | 2025-11-19 | https://www.kjzz.org/politics/2025-11-19/ | S9
ENR-AZ | ENR | Arizona advances $5.5 bn Mexico desalination proposal (IDE, 300 kAF/yr) | 2022 | https://www.enr.com/articles/55659-arizona-advances-55b-mexico-desalination-plant-proposal | S9
AZCT-25 | Arizona Capitol Times | Officials expect ~100 MGD from advanced purification facilities (Phoenix area) | 2025-04-26 | https://azcapitoltimes.com/ | S9
TWF-25 | Texas 2036 / TWDB | Texas Water Fund Proposition 4 ($1 bn/yr 2027-47) | 2025-11 | https://texas2036.org/news-analysis/proposition-4-passed-now-what/ | S9
NREL-WATER22 | Giammar et al. (NREL/LBNL), ACS ES&T Engineering | Cost and energy metrics for municipal water reuse / desalination (SWRO 3.2 kWh/m3; reuse 0.84) | 2022-03 | https://pubs.acs.org/doi/10.1021/acsestengg.1c00351 | S9
CARLSBAD | City of Carlsbad / Pumps & Systems | Carlsbad desalination 50 MGD, 13.5 kWh/kgal | 2016-2025 | https://www.carlsbadca.gov/ | S9
ACEEE-06 | ACEEE / CEC | Energy intensity of water in California (SWP up to 4,444 kWh/AF) | 2006 | https://www.aceee.org/files/proceedings/2006/data/papers/SS06_Panel12_Paper14.pdf | S9
CC-26 | Climate Central | 2025 in Review: US billion-dollar weather and climate disasters (23 events, $115 bn) | 2026-01 | https://www.climatecentral.org/report/us-billion-dollar-weather-and-climate-disasters-2025 | S10
FIRST-25 | First Street | 12th National Risk Assessment: Property Prices in Peril (55 M movers by 2055; insurance +29.4 %; $1.47 tn) | 2025-02-03 | https://firststreet.org/press/climate-driven-population-shifts-and-insurance-increases-are-set-to-erase-14-trillion-in-american-real-estate-value | S10
CENSUS-26 | U.S. Census Bureau | Vintage 2025 population estimates (growth 0.5 %; NC +84k, SC +67k domestic migration) | 2026-01-27 | https://census.gov/newsroom/press-releases/2026/population-growth-slows.html | S10
DUKE-25 | Duke Energy Florida | Storm hardening within a $16 bn five-year capital plan | 2025 | https://news.duke-energy.com/ | S10
ENTERGY-22 | Entergy | $15 bn / 10-year resilience plan | 2022 | https://www.entergy.com/ | S10
DELOITTE-26 | Deloitte Insights | 2026 Power and Utilities Industry Outlook (peak +26 % by 2035) | 2025-12 | https://www.deloitte.com/us/en/insights/industry/power-and-utilities/power-and-utilities-industry-outlook.html | S10
NATCOMM-26 | Nature Communications | Efficiency-weighted cooling degree days (CDD +10-80 % North America) | 2026 | https://www.nature.com/articles/s41467-026-75388-9 | S10
EO-14421 | White House (via McGuireWoods, Cooley) | EO 14421 Declaring a National Emergency to Secure the US Bulk-Power System; DOE RFI DOE-HQ-2026-1123 | 2026-08-26 / 2026-09-09 | https://www.mcguirewoods.com/ ; https://www.cooley.com/ | S11
BAKERTILLY | Baker Tilly | Understanding foreign entity of concern rules (MACR table) | 2026 | https://www.bakertilly.com/insights/understanding-foreign-entity-of-concern | S11
BNEF-BAT25 | BloombergNEF (via ESS News / Energy-Storage.News) | Battery price survey Dec 2025 ($108/kWh pack; stationary $70; NA +44 %) | 2025-12-09 | https://www.ess-news.com/2025/12/09/ | S11
GATEWAY-26 | Gateway Lines | Section 301 / 122 tariff tracker for Chinese batteries (low-authority) | 2026-09-18 | https://gatewaylines.com/ | S11
WM-INV26 | Wood Mackenzie via PV Tech | US inverter manufacturing can meet demand; western premium ~2 % of capex | 2026-08-07 | https://www.pv-tech.org/ | S11
WM-TRAFO | Wood Mackenzie | Transformer lead times 128-144 weeks; prices +77 % / +45 % since 2019 | 2025 | https://www.woodmac.com/ | S11
INDSAGE-26 | IndustrialSage | Power transformer lead times / US grid shortage | 2026-05-06 | https://industrialsage.com/power-transformer-lead-times-us-grid-shortage/ | S11
ACP-26 | American Clean Power (Energy-Storage.News) | Domestic BESS manufacturing capacity (modules 75 -> 180 GWh; cells 20 -> 140 GWh by 2028) | 2026-05-27 | https://www.energy-storage.news/ | S11
WM-ESM26 | Wood Mackenzie / ACP | US Energy Storage Monitor Q1/Q2 2026 (18.9 GW 2025; 2026 below 2025) | 2026-03-25 / 2026-06-23 | https://www.energy-storage.news/ | S11
IIR-26 | Industrial Info Resources | Transformer manufacturing investments ~$2 bn tracked | 2026-08-17 | https://www.industrialinfo.com/ | S11
WM-DC26 | Wood Mackenzie | US large-load requests 1,066 GW vs 298 GW committed (28 %) | 2026-08 | https://www.woodmac.com/ | S12, S13
BERNSTEIN-26 | Bernstein (press) | 135 of 492 GW data-center pipeline credible | 2026 | n/a (secondary) | S12
SIGHTLINE-26 | Bloomberg / Sightline Climate | ~4 GW data centers under construction vs 12 GW planned for 2026 | 2026-04 | https://www.bloomberg.com/ | S12
TSMC-AR24 | TSMC | 2024 Annual Report / ESG report (37.1 kWh per 12-inch wafer mask layer) | 2025-04 | https://investor.tsmc.com/static/annualReports/2024/english/pdf/2024_tsmc_ar_e_ch7.pdf | S13
TSMC-AZ | TSMC Arizona | Six logic fabs, two packaging plants, R&D ($165 bn) | 2025-03 | https://www.tsmc.com/static/abouttsmcaz/index.htm | S13
MICRON-26 | Micron / NIST / NYS PSC / ENR | Clay NY megafab ($100 bn; groundbreaking 2026-01-16; 345 kV laterals approved Oct 2025) | 2025-10 / 2026-01 | https://www.nist.gov/chips/micron-new-york-clay | S13
INTEL-OH | Intel | Ohio One fabs delayed to 2030-31 | 2025 | https://www.intel.com/ | S13
CENTURY-26 | Century Aluminum / EGA / DOE | Inola OK smelter 750 kt/yr; construction from end-2026; PSO power agreement pending | 2026-01-26 | https://centuryaluminum.com/investors/press-releases/ | S13
IAI | International Aluminium Institute | Primary aluminium smelting energy intensity statistics (~14 MWh/t) | 2025 | https://international-aluminium.org/statistics/primary-aluminium-smelting-energy-intensity/ | S13
RTOI-26 | RTO Insider / Latitude Media | ERCOT large-load queue 410-474 GW (~90 % data centers) | 2026-09 | https://www.rtoinsider.com/ | S13
ERCOT-26 | ERCOT | Large Load update to Senate Business & Commerce (Apr 2026) | 2026-04-01 | https://www.ercot.com/files/docs/2026/04/01/ERCOT_LargeLoad_Update_April2026_B-C_-Hearing.pdf | S13
IRS-45Q | IRS / OBBBA | 45Q after OBBBA: $85/t point-source, $180/t DAC, 12-year term, indexed from 2027 | 2025-07 | https://www.irs.gov/credits-deductions/credit-for-carbon-oxide-sequestration | S14
NETL-23 | NETL | Cost and Performance Baseline for Fossil Energy Plants, Rev 3 (NGCC + 90 % capture $2,049/kW; $55-61/t) | 2023 | https://netl.doe.gov/energy-analysis/ | S14
OCED-25 | DOE OCED | Termination of CCS demonstration awards (Sutter, Baytown, Cane Run) | 2025-05-30 | https://www.energy.gov/oced/ | S14
META-26 | Meta | Up to 6.6 GW nuclear by 2035 (Vistra, Oklo, TerraPower) | 2026-01-09 | https://about.fb.com/news/ | S7, S14
DOE-LOANS26 | DOE Loan Programs Office | Crane (TMI-1) $1 bn; Duane Arnold $1.9 bn (COD 2029) | 2025-11 / 2026-09-10 | https://www.energy.gov/lpo/ | S14
FERVO-26 | Fervo Energy | Cape Station 500 MW; Google 396 MW PPA | 2026-09-01 | https://fervoenergy.com/ | S14
DOE-UPRISE26 | U.S. DOE | UPRISE nuclear uprate initiative (+2.5 GW by 2027, +5 GW by 2029) | 2026-03 | https://www.energy.gov/ne/ | S14
NUC-TRACKER26 | Industry trackers (ANS / Utility Dive) | Hyperscaler nuclear deals: 9.8 GW in 13 deals | 2026 | https://www.ans.org/news/ | S14
EIA-100PCT | U.S. EIA / state statutes | States with 100 % clean electricity targets (NY 2040, CT 2040, NJ 2035, CA 2045, WA 2045, OR 2040, VA 2045/50) | 2025 | https://www.eia.gov/todayinenergy/ | S14
IEA-WEI26 | IEA | World Energy Investment 2026 ($3.4 tn total; clean $2.2 tn) | 2026-05-28 | https://www.iea.org/reports/world-energy-investment-2026 | S14
FEL-NUCANN | SE / data repo | nuclear_announced sensitivity (+19.1 GW announced nuclear by 2035) | 2026-08 | data repo Par_TotalAnnualMinCapacity/NorthAmerica_nuclear_announced | S14
FEL-BASE | FEL 2026 base | base_fel_v260707_v2.xlsx converted demand (v6c input dump) | 2026-07 | data repo NA_inputs/base_fel_v260707_v2.xlsx | all
FEL-GRIDLOW | FEL 2026 / data repo | grid_low sensitivity (IC growth 0.75 %/yr) | 2026-07 | data repo | S6
EEI-24 | Edison Electric Institute | EV Forecast & Infrastructure Report (7.7 M / 46 % 2030; 12.2 M / 72 % 2035; 78.5 M stock 2035) - pre-OBBBA | 2024 | https://www.eei.org/ | S1
NASEM-DAC | NASEM / Climeworks | Direct air capture energy intensity ~1.5-2.5 MWh/t CO2 | 2019-2025 | https://nap.nationalacademies.org/ | S4
IDRA-25 | IDRA / GWI | Desalination & Reuse Handbook 2025-2026 (Israel ~2 Mm3/d, Gulf ~20 Mm3/d context) | 2025-10-17 | https://idadesal.org/ | S9
FEL-DCHL | FEL 2026 / data repo | NorthAmerica_dc_high_limitless sensitivity (build limits mostly lifted) | 2026-07 | data repo | S3
FEL-GRIDHIGH | FEL 2026 / data repo | grid_high sensitivity (IC budget 2x by 2040) | 2026-07 | data repo | S8, S14
USER | SE / user | Fusion capex, FOM and first-commercial-year estimates (to be provided) | 2026-09 | - | S7

## Model baseline
Item | Detail | a | b | c | d
FEL26 base demand as loaded (busbar TWh)
Category | Scope | 2025 | 2030 | 2035 | 2040
Power_General | US 9 pools | 3316 | 3492 | 3944 | 4369
Power_General | Canada | 513 | 518 | 522 | 525
Power_DataCenter | US 9 pools | 133 | 726 | 1344 | 1817
Power_DataCenter | Canada | 17 | 71 | 178 | 269
Power_Buildings_Heat | US 9 pools | 764 | 735 | 710 | 709
Power_Buildings_Heat | Canada | 12 | 18 | 25 | 34
Power_Hydrogen | US 9 pools | 2 | 6 | 6 | 6
Power_Hydrogen | Canada | 0 | 3 | 5 | 9
Power_BEVs | US 9 pools | 25 | 71 | 213 | 442
Power_BEVs | Canada | 3 | 14 | 37 | 62
Power_DataCenter by region (TWh) | Region | 2025 | 2030 | 2040
| California | 4.7 | 9.2 | 26.8
| Canada | 17.1 | 70.9 | 269.3
| ERCOT | 15.6 | 268.6 | 630.5
| MISO | 14.2 | 53.8 | 146.2
| NewEngland | 0.7 | 0.7 | 1.2
| NewYork | 0 | 5.4 | 12.8
| PJM | 46.4 | 205.9 | 552.9
| SERC | 13.3 | 63.4 | 167.8
| SPP | 9.2 | 72.9 | 171.3
| WECC | 29.3 | 46 | 107.7
Model facts
Geography | 9 US pools (California, WECC, ERCOT, SPP, MISO, SERC, PJM, NewYork, NewEngland) + Canada as ONE node; no state or province resolution.
Horizon / resolution | Annual 2025-2040, 49-hour-step dispatch (179 slices), one weather year (2015). Nothing after 2040 is visible.
Demand categories | Power_General, Power_DataCenter, Power_Buildings_Heat, Power_Hydrogen, Power_BEVs (Power_Buildings_Cooling exists but is empty). Each has its own hourly profile: BEV (charging shape), Buildings_Heat and Buildings_Cooling are real profiles; DataCenter and Hydrogen are FLAT (no electrolysis flexibility, no DC load-following).
Demand source | FEL 2026 Power Demand Model workbook (base_fel_v260707_v2.xlsx: sectors buildings / industry / transport / hydrogen / data_centers, sub-segments, busbar TWh per pool) converted by NA_inputs/convert_fel_to_demand.py. Demand scenarios are best produced as FEL presets (bev_share, dc_scenario, hydrogen_scenario, industry_electrification_*, gdp_growth); fallback = scaling sub-segments on our side.
Supply guardrails | Capacity funnels from the US Pools announced pipeline (TotalAnnualMin/MaxCapacity, +-2 % to 2028 widening to -10 %/+30 % at 2035), gas retirement schedule, IC trade growth 4 %/yr, RES potentials (restool). SMR: 0 before 2033, 2.9 GW 2035, 18.7 GW 2040 max. P_Gas_CCS, P_Geothermal (conventional), P_CSP, P_H2_OCGT: capacity max 0 (disabled). EGS classes, Li-ion (max 120->404 GW), Redox flow (from 2030), CAES, PHS available.
Costs | LCOE model v1.4 capex/FOM/WACC-as-discount-rate (5 % uniform). Capex 2025 EUR/kW: CCGT 827, OCGT 691, nuclear and SMR 9091 (flat), gas CCS 2593, PV 427, onshore 1073, Li-ion 195 /kW + 964 M EUR/PJ. Fuel: Henry-Hub path folded into gas VariableCost (3.7/4.8/4.8/4.4 EUR/GJ 2025/30/35/40), regional hub factors (Canada).
Emissions / policy | No CO2 price and no emission cap in the NA data (parameters EmissionsPenalty, AnnualEmissionLimit, RegionalAnnualEmissionLimit exist but are sentinels). No RPS/CES constraints. 45Q/45V/45Y not represented.
Gas infrastructure | Optional NorthAmerica_gas data scenario (2026-09-15): R_Gas regional supply curves, 30 pipeline corridors, LNG export demand, storage, deliverability caps -> endogenous regional gas prices (2.3-3.3 EUR/GJ, i.e. below the folded HH path).
Run cost | ~1 h per 49-hour-step investment run (build 15 min + solve 12-55 min), single DuckDB writer -> serial runs. 14 scenarios x 1-2 variants = 20-30 runs = 1-2 days.
Basis | v6 (frozen July 2026, code-consistent baseline fel2026_base_49_2015_v6c) or v7 (LCOE v1.4 costs, RES cost re-anchoring; user still reviewing RES capacity shifts). Decision needed before implementation.

## Existing sensitivities
Sensitivity (v6 set) | Definition
dc_high | DC US 2035/2040 = 2188/3585 TWh; funnel max raised with ratio
dc_low | DC US 2035/2040 = 805/874 TWh; gas min floor 0
recession | GDP-recession FEL demand: DC 1048/1563, General -1..2 %
btm_lag | DC 1526/2163 (BTM lag -> more grid load)
economic | funnel widened after 2030 (min x0.75, max x1.5)
grid_high/grid_low | IC growth 2x budget / capped 0.75 %/yr
bess_optimistic/pessimistic | Li-ion cost x0.4 by 2040 + 7 h / min blend x0.53
nuclear_announced (+ccgtrelax) | +19.1 GW announced nuclear (large+SMR) by 2035 on top of the corridor, CCGT min relaxed
space_dc / disruptive / spacex | orbital compute REMOVES 5 / 13 / 27 % of US DC load by 2040 (1724/1585/1353 TWh)
gas (NorthAmerica_gas) | explicit gas supply, pipelines, LNG exports, storage, deliverability caps; endogenous regional gas prices

## Open questions
# | Scenario | Question | Why it matters
1 | all | Basis: v6 freeze (comparable to the published v6 set) or v7 (LCOE v1.4 costs, RES re-anchoring, still under review)? | Every scenario needs a reference run.
2 | all | Run budget: ~1 h per run, serial. 14 scenarios x 2-4 variants = 35-50 runs. First wave proposal: 1A, 2A, 3A, 4C, 5A, 6C, 7B, 8C, 9C, 10C, 11A, 12A, 13A, 14A (one per scenario, 14 runs), stretch variants second. | Sequencing.
3 | 7 | Fusion: capex path (central/low), FOM, first commercial year, and whether a max-build path or unlimited build is wanted. | Fills the USER INPUT rows.
4 | 8 | Canada DC base: keep the FEL path (269 TWh 2040) as the base and run 8C above it, or re-base to the announced pipeline (8A) and run 8C as the tailwind? | Defines the reference for scenario 8 deltas.
5 | 3 / 12 | DC variants from FEL presets (dc_scenario high/low) or from the external-anchored paths proposed here? | Consistency with published FEL numbers vs traceability.
6 | 2 | Flat electrolysis load for the first runs (2A-2C), or build the flexible-electrolyser technology first (2D)? | Capacity results differ materially at 300-550 TWh.
7 | 6 | Which Hormuz variant set: 6A/6B/6C/6D all, or a subset? Recession FEL acceptable as the demand leg? | Run count and the NorthAmerica_gas dependency for 6A.
8 | 10 | Relocation dials 2/4 % (10A) and 10/20 % (10C) acceptable, or other levels? | Scenario definition.
9 | 13 | Does the FEL base industry growth already contain announced fabs and smelters? | Adder size; needs the FEL team.
10 | 14 | CO2 price path and start year; nuclear ITC in LCOE v1.4 capex; CCS retrofit technology wanted in 14A or only in 14C? | Defines 14A.
11 | 11 | Is an exogenous "rip-and-replace" capex report (11C) wanted? | Deliverable scope.
12 | 4 | Run 4C with or without the orbital-compute reduction (or both)? | Sign of the space scenario.
13 | 1 / 6 | Couple the oil shock to EV adoption (6D includes 1A)? | Cross-scenario coupling.
14 | 5 | Supply-side brake on RES (funnel max = pipeline) included in 5A, or DC + gas only? | 5A definition.